## Cover
Heat-Driven Comfort & Water — Parameter Register
Every quantitative claim in the document lineage, in one traceable workbook, with live re-derivations of the headline numbers.
Workbook revision | 1.1
Source document set | lineage v1.2 (docs 00 v1.2 · 10 v1.1 · 11 v1.1 · 12 v1.4 · 20 v1.1 · 21 v1.0 · 22 v1.1 · 30 v1.2 · 31 v1.0 · 40 v1.4 · 50 v1.2)
Repository | github.com/phicyclist/slice-cooling
Concept DOI (all versions) | 10.5281/zenodo.21544099
Version DOI (v1.0 record) | 10.5281/zenodo.21544100
Governing design point | DP-A · 32 °C / 80% RH · ω 24.2 g/kg · dew point 28.1 °C · raw-water sink ~29 °C
Status of the work | Paper design. NOTHING HAS BEEN BUILT. No figure here is a measurement unless its grade says 'measured'.
Licensing | Hardware CERN-OHL-P v2 · documentation & this workbook CC-BY-4.0 · generator script MIT (LICENSE.md)
Disclosure | Open defensive publication. No patents sought or held.
Generated by | scripts/build_parameter_workbook.py — regenerate rather than hand-edit
SAFETY — binding on any build (doc 00 §8)
CO₂ interlock (<1,000 ppm target / 2,000 alarm / per-room maximum sensing / mechanical minimum stop) · no combustion appliances in the envelope · aerosol and slip assays before any cabin connection · potability and TDS tests before any water is drunk · crystallization interlock · two-worlds materials rule. Any build omitting these departs from this design.
SHEET INDEX
Sheet | Contents
Legend | Confidence grades, column definitions, cell conventions, unit policy
Design Point | The named constants every calculation sheet references
Register | Master parameter register — filterable, one row per published value
Psychrometrics | Magnus formulation; converter; saturation table validated against doc 00 §2
Model 00§4 | The generalized airflow–moisture model, solved live for three topologies
Liquid Sizing | Mixed-mode removal, regeneration, reserve and rejection — live from DP-A
Solid Sizing | Duty → inventory → coated area → condensate balance, with the F3 penalty
CO2 & Ventilation | Dose–response ladder, ERV economics, scrubber duty — live
Heat & Water | Daily heat budget, collector/fuel sizing, water redundancy ladder
Upgrade Paths | X12 lift-ceiling inequality and the MVR pressure ratio, solved live
Test Program | Tests A–L and T/M series with costs, durations, and the live budget sum
Findings | F1–F6, X1–X12, X14, spec P17 — status and where each lives
Safety & Materials | The binding register and the two-worlds materials law
Checks | Consistency observations raised while compiling this register
Sources | Document set, versions, and scope

## Legend
Legend & conventions
How to read — and how to extend — this register.
Confidence grade | Meaning | Rule
measured | A number this project has physically measured | None yet — the program is unbuilt
measured (lit.) | Measured by others and cited | Cite the regime; literature values rarely transfer across purge humidity
procurement-grade | From a datasheet, COA, or supplier quote | Verify per lot; hydrate assays drift
sizing-grade | Derived from first principles or published correlations | Usable for sizing, never for acceptance
estimate-grade | Doc 31 upgrade paths — no bench basis at all | Never load-bearing for any DP-A claim
PENDING <test> | Explicitly gated on a named experiment | Do not upgrade the grade without the result
requirement | A specification the design must meet | Binding; changes require a version bump
governing / platform | Fixed by the design point or the platform definition | Changing one invalidates every derived number
rejected / superseded | Retained as the record of what was tried | Kept visible on purpose — the correction trail
CELL CONVENTIONS
Blue bold on pale fill | INPUT — safe to change; every calculation downstream follows
Plain right-aligned | CALCULATED — a live formula; do not overwrite
Grey italic | PUBLISHED value quoted from the documents for comparison
OK / REVIEW | Automatic check: calculated vs published within ±10%
VALUE vs MIN/MAX | A single-point figure goes in VALUE; a published band goes in MIN and MAX
Units | SI throughout; humidity ratio in g/kg dry air, heat in kW and kWh/day, concentration in wt%, CO₂ in ppm by volume
Traceability | Every register row names its source document and section. If a row has no source, it does not belong here
Recalculation | The workbook is saved with full-calculation-on-load; formulas re-solve when opened

## Design Point
Design point & named constants
DP-A is the sole design point — the continuous-duty maximum for every mode. Change a blue cell and every calculation sheet follows.
AMBIENT — DP-A (doc 00 §2)
Ambient dry-bulb | 32 | °C | Sole design point; excursions are transient, never a sizing basis
Ambient relative humidity | 0.8 | — | Entered as a fraction
Raw-water sink | 29 | °C | Marine tropical surface; land sinks often cooler = margin
Atmospheric pressure | 101.325 | kPa | Magnus basis for every ω conversion
Partial-pressure denominator used in doc 12 | 97.5 | kPa | Doc 12 §1 divides by 97.5 kPa (P_atm − Pv) rather than P_atm — reproduced here for traceability
PLATFORM
Conditioned volume | 100 | m³ | Yacht interior / small dwelling / cabin / shelter
Occupants | 4 | person
Latent generation per occupant | 70 | g/h | 50 sleeping · 90 active; ±30% band
Peak sensible load (solid track) | 3.5 | kW | Solar noon, ~100 m³ envelope
Fresh-air floor | 48 | m³/h | 12 m³/h·person — CO₂-interlocked, mechanical minimum stop
CO₂ generation, crew total awake | 0.072 | m³/h | 0.047 asleep; ≈3.4 kg/day
Outdoor CO₂ baseline | 400 | ppm
CO₂ specification (P17) | 1000 | ppm | Safety-critical, all modes including sealed
COMFORT TARGETS
Cabin target, liquid track | 29 | °C | At 55% RH → ω 13.8 g/kg
Cabin target RH, liquid track | 0.55 | —
Cabin target, solid track | 25 | °C | 40–55% RH band
SORBENT BACK-ENDS
Water activity, 40 wt% CaCl₂ | 0.45 | — | PENDING test A — ±0.05 is the largest single unknown
Water activity, 43–44 wt% CaCl₂ | 0.34 | — | PENDING test A — the hot-regen lever
Brine temperature at the contactor | 30 | °C | Sink 29 °C + approach; drives the floor band
Strong-brine concentration | 40 | wt%
Dilute-brine concentration | 35 | wt%
Supply humidity ratio, solid track | 8 | g/kg | AlFu back-end — the model's only sorbent input
EFFECTIVENESS & EFFICIENCY
ERV latent effectiveness | 0.8 | — | PENDING test E; ≥0.8 is the X7 basis
M-cycle dew-point effectiveness | 0.7 | — | 0.65–0.80 band; 0.70 is the model value
Liquid regeneration thermal COP | 0.59 | — | Build-up in doc 12 §1; 0.65 with a recovery HX
Solid specific regeneration energy | 0.85 | kWh/L | 0.8–1.0 band; latent floor is 0.67
PHYSICAL CONSTANTS (do not edit)
Magnus coefficient A | 0.61094 | kPa | Psat = A·exp(B·T/(T+C)), T in °C
Magnus coefficient B | 17.625 | — | Alduchov–Eskridge form
Magnus coefficient C | 243.04 | °C
Mass ratio water/dry air | 0.622 | — | M_w/M_a = 18.015/28.964
Specific heat, dry air | 1.006 | kJ/kg·K
Specific heat, water vapour | 1.86 | kJ/kg·K
Latent heat at 0 °C | 2501 | kJ/kg | Enthalpy datum for the moist-air chain
Latent heat at regeneration | 2440 | kJ/kg | 2.44 MJ/kg — the doc 10 §3 basis
Absorption heat into brine | 2700 | kJ/kg | 2.7 MJ/kg — exceeds latent by the heat of dilution
Air density at DP-A (physical) | 1.164 | kg/m³ | Dry air at 32 °C, 101.325 kPa. Moist air at DP-A is lower still (~1.145)
Air density basis used in the documents | 1.208 | kg/m³ | Back-solved from doc 12's 48 m³/h → 58 kg/h and 75 → 90.6 kg/h (standard ~1.2 air). Used for the liquid mass flows so the published figures reproduce — see CHK-009
Seconds per hour | 3600 | s/h
DERIVED AT DP-A (live — these reproduce the doc 00 §2 / doc 12 §1 headline figures)
Saturation pressure at ambient |  | kPa | Magnus at 32 °C — doc 12 quotes 4.76
Ambient vapour pressure |  | kPa | Doc 12 quotes 3.81
Ambient humidity ratio |  | g/kg | Doc 00/12 publish 24.2
Ambient ω on the doc-12 denominator |  | g/kg | The 0.622·3.81/97.5 form quoted in doc 12 §1
Ambient dew point |  | °C | Doc 00 publishes 28.1
Cabin ω, liquid target |  | g/kg | Doc 12 publishes 13.8
Saturation ω at the sink |  | g/kg | Doc 00 publishes 25.6 — the working-exhaust state
ERV pre-dried fresh air |  | g/kg | Doc 12 publishes 15.9 at ε 0.8 — see Checks CHK-002
Fresh-air mass flow |  | kg/h | Doc 12 quotes ≈58 kg/h
Cabin latent gains |  | g/h | Doc 12 quotes 280 g/h

## Register
Master parameter register
One row per published quantitative claim. Filter by track, category, grade, or gating test. Every row names its source — a row without a source does not belong here.
Rows: 265
ID | Track | Category | Parameter | Symbol | Value | Min | Max | Unit | Confidence | Gate | Basis / derivation | Source
DP-001 | Shared | Design point | Ambient dry-bulb (DP-A) | T_amb | 32 |  |  | °C | governing |  | Sole continuous-duty maximum rating point for every mode | 00 §2
DP-002 | Shared | Design point | Ambient relative humidity (DP-A) | RH_amb | 80 |  |  | % | governing |  |  | 00 §2
DP-003 | Shared | Design point | Ambient humidity ratio | ω_amb | 24.2 |  |  | g/kg | governing |  | Psat 4.76 kPa → Pv 3.81 → 0.622·3.81/97.5 | 12 §1
DP-004 | Shared | Design point | Ambient dew point | T_dp | 28.1 |  |  | °C | governing |  | Sits at/above every ambient sink — the floor a desiccant breaks | 00 §2
DP-005 | Shared | Design point | Ambient wet-bulb | T_wb | 29.5 |  |  | °C | sizing-grade |  |  | 20 §1
DP-006 | Shared | Design point | Raw-water sink temperature | T_sink | 29 |  |  | °C | governing |  | Tropical surface/mixed layer; land sinks often cooler = margin | 00 §1
DP-007 | Shared | Design point | Atmospheric pressure | P_atm | 101.325 |  |  | kPa | reference |  | Magnus basis for all ω conversions | 00 §2
DP-008 | Shared | Design point | Conditioned volume (reference) | V_cab | 100 |  |  | m³ | platform |  | Yacht interior / small dwelling / cabin / shelter | 20 §1
DP-009 | Shared | Design point | Occupants (reference) | n | 4 |  |  | person | platform |  |  | 20 §1
DP-010 | Shared | Design point | Retired secondary design point | — |  | 30 | 75 | °C / % | historical |  | Retired; numbers derived from it survive only in archived docs | 00 §2
DP-011 | Shared | Psychrometrics | Saturation humidity ratio at 26 °C | ω_sat | 21.3 |  |  | g/kg | reference |  | Magnus, 101.325 kPa | 00 §2
DP-012 | Shared | Psychrometrics | Saturation humidity ratio at 27 °C | ω_sat | 22.6 |  |  | g/kg | reference |  |  | 00 §2
DP-013 | Shared | Psychrometrics | Saturation humidity ratio at 28 °C | ω_sat | 24.1 |  |  | g/kg | reference |  |  | 00 §2
DP-014 | Shared | Psychrometrics | Saturation humidity ratio at 29 °C | ω_sat | 25.6 |  |  | g/kg | reference |  | Working-air exhaust state in the solid balance | 00 §2
DP-015 | Shared | Psychrometrics | Saturation humidity ratio at 30 °C | ω_sat | 27.1 |  |  | g/kg | reference |  |  | 00 §2
DP-016 | Shared | Loads | Occupant latent generation (average) | m_lat | 70 | 50 | 90 | g/h·person | sizing-grade |  | 50 sleeping / 90 active; ±30% on load | 10 §1; 12 §3
DP-017 | Shared | Loads | Cabin latent gains, 4 adults | G_lat | 280 |  |  | g/h | sizing-grade |  | 4 × 70 g/h·person | 12 §1
DP-018 | Solid | Loads | Peak sensible load (solar noon) | Q_sens | 3.5 |  |  | kW | sizing-grade |  | ~100 m³ envelope at DP-A | 20 §1
DP-019 | Solid | Loads | Envelope + occupant latent | G_lat | 2 | 1.8 | 2.8 | kg/h | sizing-grade |  | Central 2.0; the naive (and wrong) sizing basis — see F1 | 20 §1
DP-020 | Shared | Loads | Infiltration, unattended | ACH | 0.1 | 0.05 | 0.15 | 1/h | sizing-grade |  | One vs two contactors turns on this band | 12 §3
DP-021 | Liquid | Comfort | Comfort target, liquid track | T/RH | 29 |  |  | °C | requirement |  | 29 °C / 55% RH → ω 13.8 g/kg | 10 §1
DP-022 | Liquid | Comfort | Comfort target humidity ratio | ω_cab | 13.8 |  |  | g/kg | requirement |  | Psat 4.01 → Pv 2.20 at 29 °C / 55% | 12 §1
DP-023 | Solid | Comfort | Comfort target, solid track | T | 25 |  |  | °C | requirement |  | ~40–55% RH | 20 §1
DP-024 | Solid | Comfort | Cabin steady state, solid track | ω_cab | 9.1 |  |  | g/kg | sizing-grade | T2 | ~40% RH — drier than target; headroom for a warmer setpoint | 20 §5
LQ-001 | Liquid | Brine | Working concentration, strong | c_hi | 40 |  |  | wt% | sizing-grade | A | Water activity aw ≈ 0.45 | 10 §2
LQ-002 | Liquid | Brine | Working concentration, dilute | c_lo | 35 |  |  | wt% | sizing-grade | A |  | 10 §2
LQ-003 | Liquid | Brine | Water activity, 40 wt% | aw | 0.45 |  |  | — | PENDING A | A | Published data ±0.05 aw — the largest single unknown | 12 §3
LQ-004 | Liquid | Brine | Water uptake per kg concentrate | Δm | 0.143 |  |  | kg/kg | sizing-grade |  | c_hi/c_lo − 1 = 0.40/0.35 − 1 | 10 §3
LQ-005 | Liquid | Brine | Absorber outlet floor, 40 wt% @ 30 °C brine | ω_out | 11.9 | 10 | 14.2 | g/kg | PENDING A/I | A, I | Temperature-dependent band: 10.0 @27 °C, 14.2 @33 °C | 12 §1
LQ-006 | Liquid | Brine | Hot-regen concentration | c_hi |  | 43 | 44 | wt% | sizing-grade | D | aw 0.33–0.35 at 85–93 °C regeneration | 10 §3
LQ-007 | Liquid | Brine | Absorber outlet floor, 43–44 wt% @ 30 °C | ω_out | 9 | 7.5 | 9 | g/kg | PENDING A | A | 7.5 g/kg at 27 °C brine | 12 §1
LQ-008 | Liquid | Brine | Cooling leverage on the floor | ∂ω/∂T |  | 0.5 | 0.7 | g/kg·K | sizing-grade | A | ∂w_eq/∂T at aw 0.45; land cool-water sinks exploit it free | 10 §3
LQ-009 | Liquid | Brine | Crystallization liquidus, 40 wt% | T_liq |  | 12 | 13 | °C | procurement-grade |  | CaCl₂ solubility curve; erratum 5 corrected this from ~5 °C | 12 §1
LQ-010 | Liquid | Brine | Crystallization liquidus, 42 wt% | T_liq |  | 18 | 19 | °C | procurement-grade |  |  | 12 §1
LQ-011 | Liquid | Brine | Crystallization liquidus, 44 wt% | T_liq | 22 |  |  | °C | procurement-grade |  |  | 12 §1
LQ-012 | Liquid | Safety | High-SG cutoff concentration | c_max | 42 |  |  | wt% | requirement |  | Interlock: unless brine ≥22 °C guaranteed (safety register 6) | 11 §4
LQ-013 | Liquid | Safety | Stored concentrate cap | c_store | 43 |  |  | wt% | requirement |  |  | 11 §4
LQ-014 | Liquid | Brine | Salt specification | — |  | 94 | 97 | % | procurement-grade |  | Plain CaCl₂ pellet 94–97% or flake 83–87%; no ferrocyanide/dye/MgCl₂ | 11 §1
LQ-020 | Liquid | Air path | Fresh-air floor, 4 occupants | V_fresh | 48 |  |  | m³/h | requirement |  | 12 m³/h·person, CO₂-interlocked; ≈58 kg/h | 12 §1
LQ-021 | Liquid | Air path | Recirculation flow (mixed mode) | V_rec | 75 |  |  | m³/h | sizing-grade | I | Decouples removal capacity from the ventilation ration (X6) | 10 §2
LQ-022 | Liquid | Air path | Total absorber flow (mixed mode) | V_tot | 123 |  |  | m³/h | sizing-grade | I | ≈147 kg/h; = gains 280 g/h ÷ (13.8 − 11.9) g/kg | 12 §1
LQ-023 | Liquid | Air path | ERV latent effectiveness | ε_lat | 0.8 |  |  | — | PENDING E | E | Purchasable with membrane area — oversize it | 11 §5
LQ-024 | Liquid | Air path | ERV pre-dried fresh air | ω_ERV | 15.9 |  |  | g/kg | sizing-grade | E | ω_amb − ε(ω_amb − ω_cab) at ε 0.8 — see CHK-002 | 12 §1
LQ-025 | Liquid | Air path | ERV CO₂ crossover (EATR) limit | EATR | 5 |  |  | % | PENDING E | E | Acceptance limit, not a prediction | 11 §5
LQ-026 | Liquid | Duty | Peak removal, 4 adults, mixed mode (bare fresh) | ṁ_w | 0.88 |  |  | kg/h | sizing-grade | I | 58 kg/h × (24.2−11.9) + 90.6 kg/h × (13.8−11.9) | 12 §1
LQ-027 | Liquid | Duty | Peak removal, ERV'd steady | ṁ_w | 0.49 | 0.49 | 0.6 | kg/h | sizing-grade | E, I | Quoted 0.49 corresponds to ω_ERV ≈ 17.4 g/kg — see CHK-002 | 12 §1
LQ-028 | Liquid | Duty | Regeneration latent duty | Q_lat | 0.6 |  |  | kW | sizing-grade |  | 0.88 kg/h × 2.44 MJ/kg | 10 §3
LQ-029 | Liquid | Duty | Regeneration heat, peak (bare fresh) | Q_regen | 0.92 |  |  | kW | sizing-grade | D | latent ÷ COP 0.55–0.75 | 12 §1
LQ-030 | Liquid | Duty | Regeneration heat, peak (ERV'd) | Q_regen | 0.6 |  |  | kW | sizing-grade | D, E |  | 12 §1
LQ-031 | Liquid | Duty | Daily regeneration heat, bare fresh | E_day |  | 17 | 20 | kWh/day | sizing-grade | D | Duty-scheduled at DP-A | 12 §1
LQ-032 | Liquid | Duty | Daily regeneration heat, ERV + DCV | E_day |  | 9 | 11 | kWh/day | sizing-grade | D, E | The budget the solar array is sized to | 12 §1
LQ-033 | Liquid | Duty | Regeneration thermal COP | COP_th | 0.59 | 0.55 | 0.75 | — | sizing-grade | D | Build-up: latent 0.678 + brine sens. 0.184 + air sens. 0.131 kWh/kg ×1.15 | 12 §1
LQ-034 | Liquid | Duty | Regeneration COP with recovery HX | COP_th | 0.65 |  |  | — | sizing-grade | D |  | 12 §1
LQ-035 | Liquid | Duty | Absorption heat rejected to brine | Q_abs | 0.66 |  |  | kW | sizing-grade |  | 0.88 kg/h × 2.7 MJ/kg — rejection is required, not optional (erratum 2) | 12 §1
LQ-036 | Liquid | Duty | Uncooled contactor self-heating | ΔT |  | 5 | 8 | K | sizing-grade | I | Drives the floor to 12–14+ g/kg | 12 §1
LQ-037 | Liquid | Duty | Air-side heat removal capacity | UA_air | 16 |  |  | W/K | sizing-grade |  | Per 48 m³/h fresh (≈35 W/K quoted at mixed-mode flow, 10 §3) | 12 §1
LQ-038 | Liquid | Duty | Brine transfer flow, average | V̇_b | 0.07 | 0.04 | 0.35 | L/min | sizing-grade |  | removal ÷ 0.143 ÷ ρ; 0.35 L/min peak | 10 §3
LQ-039 | Liquid | Storage | Overnight reserve, 4 adults | m_res |  | 35 | 40 | kg | sizing-grade |  | 12 h duty ÷ 0.143 kg/kg, duty-averaged | 10 §3
LQ-040 | Liquid | Storage | Reserve specification band | m_res |  | 25 | 55 | kg | requirement |  | Tank sizing spec; vented HDPE 25–60 L, tied down | 10 §3; 11 §6
LQ-041 | Liquid | Water | Still distillate output | V̇_dist |  | 8 | 18 | L/day | sizing-grade | G | Byproduct of regeneration; feeds the M-cycle and tanks | 30 §5
LQ-050 | Liquid | Contactor | Cell fill envelope | H×W×D |  |  |  | mm | sizing-grade | I | 600 H × 300 W × 150 D, cross-flow, 300 mm air path | 11 §2
LQ-051 | Liquid | Contactor | Cell rated capacity | ṁ_cell |  | 0.4 | 0.8 | kg/h | PENDING I | I | At 0.6–1 m/s face velocity — the band test I closes | 11 §2
LQ-052 | Liquid | Contactor | Face velocity, design band | v_face |  | 0.6 | 1 | m/s | sizing-grade | I |  | 11 §2
LQ-053 | Liquid | Contactor | Irrigation rate per cell | V̇_irr |  | 7 | 11 | L/min | sizing-grade | I | 150–240 L/min·m²; underwetting collapses K·a nonlinearly | 11 §2
LQ-054 | Liquid | Contactor | Internal recirculation ratio | — | 50 |  |  | passes | sizing-grade | I | Per unit concentration change — floor set by sump, not per-pass | 11 §2
LQ-055 | Liquid | Contactor | Mass-transfer coefficient (literature) | K·a |  | 1 | 3 | kg/m³·s | PENDING I | I | Spread sets contactor depth at 1–3 stages | 12 §3
LQ-056 | Liquid | Contactor | NTU for 85% approach | NTU | 1.9 |  |  | — | sizing-grade | I | Central estimate two 300 mm stages; conservative three | 11 §2
LQ-057 | Liquid | Contactor | Cabinet envelope | L×W×H |  |  |  | m | sizing-grade |  | 0.25 × 0.25 × 1.1 — slim-locker/closet class | 11 §2
LQ-058 | Liquid | Contactor | Air-side ΔP, dry fill | ΔP |  | 20 | 40 | Pa | sizing-grade | I | Turndown state (brine valved off) | 11 §2
LQ-059 | Liquid | Contactor | Air-side ΔP, film (trickle) mode | ΔP |  | 5 | 100 | Pa | sizing-grade | I | vs 1.4–2.8 kPa for bubble columns — the ~90% electrical cut | 10 §4
LQ-060 | Liquid | Contactor | Air-side ΔP, flooded (storm) mode | ΔP |  | 100 | 300 | Pa | sizing-grade | I | Level setpoint, not a gimbal; pool-class tilt tolerance | 11 §2
LQ-061 | Liquid | Contactor | Drift-eliminator carryover | — |  | 0.001 | 0.005 | % of liquid | procurement-grade | B | Chevron PVC; then PP mesh demister. No metal mesh at any grade | 11 §3
LQ-062 | Liquid | Regenerator | Sealed still pool area | A_pool |  | 0.3 | 0.5 | m² | sizing-grade | G | Shallow HDPE/PP/CPVC tray, lid sloped ≥15° | 11 §4
LQ-063 | Liquid | Regenerator | Sealed still specific rate | ṁ" |  | 1 | 2 | kg/h·m² | PENDING G | G | At design ΔT | 11 §4
LQ-064 | Liquid | Regenerator | Still tray footprint at 0.9 kg/h | A_pool |  | 0.5 | 0.9 | m² | sizing-grade | G |  | 12 §1
LQ-065 | Liquid | Regenerator | Pool vapour pressure, 60–93 °C | P_v |  | 14 | 70 | kPa | reference |  | vs sink-cooled condenser 4–5 kPa → ΔPv 10–65 kPa (X2) | 11 §4
LQ-066 | Liquid | Regenerator | Condenser vapour pressure | P_v |  | 4 | 5 | kPa | reference |  | Sink-cooled at 29 °C | 11 §4
LQ-067 | Liquid | Regenerator | Pool temperature band | T_pool |  | 60 | 93 | °C | sizing-grade | D | Rate lever, not an equilibrium wall (X2) | 11 §4
LQ-068 | Liquid | Regenerator | Still rate multiplier at 93 °C | — | 1.45 |  |  | × (85 °C) | sizing-grade | D | CPVC's only unique purchase | 11 §4
LQ-069 | Liquid | Regenerator | Still rate multiplier at 70 °C | — | 0.4 |  |  | × (85 °C) | sizing-grade | D | PP / HDPE legal | 11 §4
LQ-070 | Liquid | Regenerator | Still rate multiplier at 60 °C | — |  | 0.1 | 0.17 | × (85 °C) | sizing-grade | D | PVC (non-pressurized tray); holds mothball / 2-person duty | 11 §4
LQ-071 | Liquid | Regenerator | Air-swept exhaust humidity (degraded) | ω_exh | 98 |  |  | g/kg | sizing-grade | G | Dew point 53 °C — rains salty condensate below that (erratum 6) | 12 §1
LQ-072 | Liquid | Regenerator | Air-swept condenser recovery | Δω | 64 |  |  | g/kg | sizing-grade | G | At 34 °C approach; condensate technical-grade PENDING TDS | 12 §1
LQ-073 | Liquid | Cooling | Raw-water flow, base | V̇_rw | 300 |  |  | L/h | sizing-grade |  | 0.66 kW rejection at 2 K rise | 12 §1
LQ-074 | Liquid | Cooling | Raw-water flow, heat-rich | V̇_rw |  | 600 | 900 | L/h | sizing-grade |  | Up to ~2 kW rejection | 12 §1
LQ-075 | Liquid | Cooling | Floor penalty of 3–4 K rise | Δω | 1 |  |  | g/kg | sizing-grade |  | Halves raw-water flow — the trade is explicit | 11 §8
LQ-076 | Liquid | Electrical | Total electrical, film primary (initial) | P_e |  | 25 | 50 | W | sizing-grade |  | Fans 25–40 + recirc 15–30 + raw water 5–15 + peristaltic | 12 §1
LQ-077 | Liquid | Electrical | Total electrical, film primary (scaled) | P_e |  | 50 | 80 | W | sizing-grade |  | + ERV / exhaust fan | 12 §1
LQ-078 | Liquid | Electrical | Raw-water circuit share | P_e |  | 30 | 50 | W | sizing-grade |  | Largest single consumer at scale | 11 §8
LQ-079 | Liquid | Electrical | Column annex, drilled rings | P_e |  | 100 | 140 | W | sizing-grade | C | The reason columns are the annex, not the primary | 12 §1
LQ-080 | Liquid | Electrical | Column annex, membrane diffusers | P_e |  | 170 | 380 | W | sizing-grade | C | Avoid — diffuser dynamic wet pressure (erratum 3) | 12 §1
LQ-081 | Liquid | Columns | Superficial air velocity limit | v_s | 0.2 |  |  | m/s | sizing-grade | C | → 13.4 m³/h per 6″ column | 11 §9
LQ-082 | Liquid | Columns | Sparger static head | ΔP | 1.37 | 1.35 | 1.4 | kPa/10 cm | measured (lit.) | C | At SG 1.4 (erratum 7) | 11 §9
LQ-083 | Liquid | Columns | Membrane diffuser dynamic wet pressure | ΔP |  | 1.5 | 4 | kPa | procurement-grade | C | Rises with fouling; silently doubles blower watts | 11 §9
LQ-084 | Liquid | Columns | Drilled-ring sparger ΔP | ΔP |  | 0.3 | 0.5 | kPa | sizing-grade | C | 1 mm holes in CPVC — wins unless approach fraction says otherwise | 11 §9
LQ-085 | Liquid | M-cycle | Berth-cascade supply temperature | T_sup | 22.6 |  |  | °C | sizing-grade | H | Working air ⅓ drawn from cabin, exhausted saturated ~27 °C | 12 §1
LQ-086 | Liquid | M-cycle | Berth-cascade sensible output | Q_out | 102 |  |  | W/outlet | sizing-grade | H | vs 86 W for the rejected dry-channel bleed (X5) | 12 §1
LQ-087 | Liquid | M-cycle | Berth-cascade water draw | V̇_w | 4.1 |  |  | L/day | sizing-grade | H | ≤ still distillate — the loop closes | 12 §1
LQ-088 | Liquid | M-cycle | Dew-point effectiveness | ε_dp |  | 0.65 | 0.8 | — | sizing-grade | H |  | 10 §2
LQ-089 | Liquid | M-cycle | Supply from 11.9 g/kg feed | T_sup |  | 21 | 23 | °C | sizing-grade | H | Feed dew point 16.7 °C | 10 §2
LQ-090 | Liquid | M-cycle | Supply from 9.0 g/kg feed | T_sup |  | 18 | 21 | °C | sizing-grade | H | Feed dew point 12.5 °C (hot-regen brine) | 10 §2
LQ-091 | Liquid | M-cycle | Supply from 7.5–8 g/kg feed | T_sup |  | 15 | 18 | °C | sizing-grade | H | Feed dew point ~10 °C (LiCl blend) | 10 §2
LQ-092 | Liquid | Thermal bus | Buffer tank volume | V_buf |  | 30 | 60 | L | sizing-grade |  | Insulated, 65–90 °C; merges all sources, doubles as DHW | 11 §7
LQ-093 | Liquid | Thermal bus | Thermostatic limit valve setpoint | T_lim |  | 85 | 90 | °C | requirement |  | Protects the CPVC/PP hot side | 11 §7
LQ-094 | Liquid | Thermal bus | Solar collector area (ERV'd budget) | A_sol |  | 2.5 | 4.5 | m² | sizing-grade |  | 9–11 kWh/day ÷ 2.5–3 kWh/m²·day; ~2 m² ETC top-lift with PVT | 12 §1
LQ-095 | Liquid | Thermal bus | Diesel hydronic fuel, full duty | V̇_f |  | 1.1 | 1.4 | L/day | sizing-grade |  | ÷ 8.5 kWh/L, 5 kW heater class | 12 §1
VL-001 | Liquid | Volume ladder | Once-through cascade M-cycle cooling | V |  | 2 | 5 | m³/outlet | sizing-grade | H | 74–112 W; limit = dew point of working air | 00 §6
VL-002 | Liquid | Volume ladder | Unattended, 1 contactor, holding 13 g/kg | V | 90 |  |  | m³ | sizing-grade | I | ×2 per contactor; limit = contactor capacity vs 0.1 ACH | 00 §6
VL-003 | Liquid | Volume ladder | Unattended, 1 contactor, mold-safe | V |  | 160 | 215 | m³ | sizing-grade | I | 60–65% RH basis, ~30–50 W + trickle heat | 00 §6
VL-004 | Liquid | Volume ladder | Once-through occupied (pressure integrity) | V |  | 110 | 240 | m³ | sizing-grade | I | Supply ≥ 2–3× infiltration | 00 §6
VL-005 | Liquid | Volume ladder | Mixed-mode occupied (baseline) | V |  | 300 | 500 | m³ | sizing-grade | I | With a 3-cell bank; limit = bank capacity + heat budget | 00 §6
VL-006 | Liquid | Volume ladder | Whole-cabin AC (recirc + hot-regen brine) | V | 100 |  |  | m³ | deferred |  | ~10.6 kg/h, ~11 kW heat — converges with the solid track (X1) | 00 §6
VL-007 | Liquid | Volume ladder | Whole-cabin once-through absorber duty | ṁ_w |  | 5.5 | 11 | kg/h | sizing-grade |  | Drying 370–750 m³/h of ambient supply — why X1 holds | 12 §1
VL-008 | Liquid | Performance | 4 adults, once-through, base brine | RH |  | 59 | 66 | % | sizing-grade | I | FAILS comfort — mode retired for full occupancy (erratum 8) | 10 §5
VL-009 | Liquid | Performance | 4 adults, mixed-mode, cooled base brine | RH | 55 |  |  | % | sizing-grade | I | The occupied baseline (X6), at 29 °C | 10 §5
VL-010 | Liquid | Performance | 2 adults, once-through, cooled brine | RH |  | 54 | 58 | % | sizing-grade | I | Stands on the base system | 10 §5
SD-001 | Solid | Duty | Total peak sorbent duty (self-consistent) | ṁ_w |  | 9 | 11 | kg/h | sizing-grade | T2 | F1: working-air moisture dominates; sharpened from 7–8 kg/h | 20 §5
SD-002 | Solid | Duty | Naive envelope-only duty (cautionary row) | ṁ_w |  | 2 | 3 | kg/h | superseded |  | Under-sizes the desiccant 3–5× — retained as the error record | 22 §4
SD-003 | Solid | Duty | Continuous regeneration heat | Q_regen |  | 7.5 | 9 | kW | sizing-grade | M2, T2 | ~0.85 kWh/L × duty | 20 §5
SD-004 | Solid | Duty | Parasitic electrical | P_e |  | 0.6 | 1 | kW | PENDING M1 | M1 | Fans 300–660 W supply + 60–145 W working; pumps 100–250 W | 20 §5
SD-005 | Solid | Duty | Supply fan pressure | ΔP |  | 250 | 550 | Pa | PENDING M1 | M1 | Fan efficiency η 0.32 assumed | 20 §5
SD-006 | Solid | Duty | Working fan pressure | ΔP |  | 150 | 350 | Pa | PENDING M1 | M1 |  | 20 §5
SD-007 | Solid | Air path | Supply airflow | ṁ_a |  | 0.43 | 0.51 | kg/s | sizing-grade | T2 | ≈1,350–1,590 m³/h; topology-dependent (dry-draw vs cabin-draw) | 20 §5
SD-008 | Solid | Air path | Working airflow | ṁ_w,air |  | 0.13 | 0.16 | kg/s | sizing-grade | T2 | 400–500 m³/h; Q_wet ÷ Δh | 20 §5
SD-009 | Solid | Air path | Supply temperature | T_sup |  | 16.8 | 18.1 | °C | sizing-grade | T2 | Set by working-air dew point at ε_dp 0.7 | 20 §5
SD-010 | Solid | Air path | Post-desiccant humidity ratio | ω_sup | 8 |  |  | g/kg | sizing-grade | M1 | AlFu back-end; state 1–3 of the chain | 20 §2
SD-011 | Solid | Air path | Post-desiccant air temperature | T |  | 50 | 55 | °C | sizing-grade | M1 | Adsorption heat partly removed by sink fluid | 20 §2
SD-012 | Solid | Air path | Post-intercool temperature | T |  | 30 | 32 | °C | sizing-grade |  | Sensible only, to raw water | 20 §2
SD-013 | Solid | Air path | Working exhaust state (recycled) | ω | 25.6 |  |  | g/kg | sizing-grade |  | Saturated at 29 °C; never vented in X8 mode | 20 §2
SD-014 | Solid | Air path | M-cycle dew-point effectiveness | ε_dp | 0.7 |  |  | — | sizing-grade | H | Toward ~10.8 °C dew point on dried air | 20 §5
SD-015 | Solid | Air path | Post-ERV fresh state | T/ω | 31 | 12 |  | °C / g/kg | sizing-grade | E | Pre-dried from 24.2 g/kg at ε 0.8 | 20 §2
SD-016 | Solid | Cycle | Half-cycle time | t_half | 10 |  |  | min | sizing-grade | M2 | Throughput is governed by cycle time and coated area, not mass | 22 §1
SD-017 | Solid | Energy | Latent floor of desorption | e_lat | 0.67 |  |  | kWh/L | reference |  | Heat of vaporization — material-independent, 70–85% of input | 20 §3
SD-018 | Solid | Energy | Binding excess (sorbent-dependent) | e_bind |  | 0.05 | 0.3 | kWh/L | sizing-grade | M3 | MOF low | 20 §3
SD-019 | Solid | Energy | Sensible bed cycling | e_sens |  | 0.03 | 0.1 | kWh/L | PENDING M3 | M3 | May be optimistic for the plumbing, not just the bed (doc 20 §4) | 20 §3
SD-020 | Solid | Energy | Total specific regeneration energy | e_tot |  | 0.8 | 1 | kWh/L | PENDING M3 | M3 | The M3 acceptance figure | 20 §3
SD-021 | Solid | Energy | Recoverable fraction of input | — |  | 10 | 15 | % | sizing-grade |  | Condenser latent is downhill and DHW-demand-capped (1–3 kWh/day) | 20 §3
SD-022 | Solid | Water | Regeneration condensate | V̇_c |  | 150 | 220 | L/day | sizing-grade | T2 | Covers the M-cycle wet-channel feed | 20 §5
SD-023 | Solid | Water | Potable-grade surplus | V̇_s |  | 50 | 70 | L/day | sizing-grade | T2 | The gains + ventilation terms; water-neutral M-cycle (X8) | 20 §5
SD-024 | Solid | Regeneration | Design regeneration temperature | T_reg |  | 60 | 65 | °C | sizing-grade | M2 | Purge-humidity-dependent — the most misquoted figure in the literature | 20 §6
SD-025 | Solid | Regeneration | Representative purge humidity | ω_purge | 25 | 24 | 25 | g/kg | sizing-grade | M2 | M2 is run against ~24 g/kg logged purge, never dry lab air | 20 §6
SD-026 | Solid | Regeneration | Purge RH at bed face, 45 °C | RH_face | 38 |  |  | % | sizing-grade | M2 | Above AlFu's step — zero driving force (F2) | 20 §6
SD-027 | Solid | Regeneration | Purge RH at bed face, 50 °C | RH_face | 29 |  |  | % | sizing-grade | M2 | On the step — marginal | 20 §6
SD-028 | Solid | Regeneration | Purge RH at bed face, 60 °C | RH_face | 17 |  |  | % | sizing-grade | M2 | Below the step — works | 20 §6
SD-029 | Solid | Regeneration | Purge RH at bed face, 65 °C | RH_face | 13 |  |  | % | sizing-grade | M2 | Below the step — comfortable | 20 §6
SD-030 | Solid | Sorbent | AlFu isotherm step position | RH_step |  | 25 | 30 | % | procurement-grade | T4 | Type V; the decisive selection property | 21 §2
SD-031 | Solid | Sorbent | Working Δq, dry-purge full swing | Δq |  | 0.2 | 0.3 | g/g | procurement-grade | T4 | F3: this is NOT the sizing number — see SD-032 | 21 §2
SD-032 | Solid | Sorbent | Effective Δq under humid purge | Δq_eff |  | 0.15 | 0.2 | g/g | PENDING M2 | M2 | F3: residual 0.05–0.10 g/g at 60–65 °C → +25–50% inventory | 21 §6
SD-033 | Solid | Sorbent | Residual loading at 60–65 °C | q_res |  | 0.05 | 0.1 | g/g | PENDING M2 | M2 | Against ~25 g/kg purge | 21 §6
SD-034 | Solid | Sorbent | BET surface area, aqueous route | S_BET | 1135 | 1000 | 1135 | m²/g | procurement-grade | T4 | QC gate 4: ≥1,000; target 1,100–1,135 | 21 §6
SD-035 | Solid | Sorbent | BET surface area, grinding route | S_BET |  | 750 | 1100 | m²/g | PENDING T4 | T4 | Gate ≥750–800; expected 790–1,100 | 21 §4
SD-036 | Solid | Sorbent | Yield gate (activated dry mass) | Y | 90 |  |  | % theor. | requirement | T4 | ~158 g/mol per Al | 21 §6
SD-037 | Solid | Sorbent | Demonstrated cycle life, AlFu | N_cyc | 4500 |  |  | cycles | measured (lit.) | M4 | Unchanged; sibling CAU-10-H to 10,000. Failure mode is mechanical | 21 §2
SD-038 | Solid | Coating | Coating thickness | t |  | 0.1 | 0.5 | mm | sizing-grade | M1 | Sprayed (preferred over dip) onto prepared aluminium | 22 §2
SD-039 | Solid | Coating | Sorbent loading, planform | m" | 0.18 |  |  | kg/m² | sizing-grade | M1 |  | 22 §2
SD-040 | Solid | Coating | PVA hydrolysis grade | — |  | 98 | 99 | % | requirement | M4 | Fully hydrolyzed only — partial grades redissolve in humid service | 22 §2
SD-041 | Solid | Coating | Binder fraction | w_b | 10 |  |  | wt% | sizing-grade | M4 | Nominal; locked by test | 22 §2
SD-042 | Solid | Coating | Anneal / activation temperature | T_act |  | 120 | 150 | °C | requirement |  | 6–12 h; doubles as the mandatory PVA anneal — a re-coat never skips it | 22 §2
SD-043 | Solid | Sizing | Sorbent inventory, envelope-only basis | m_s |  | 3 | 4 | kg | superseded | T2 | Cautionary row; real charge is 3–5× this, then +25–50% for F3 | 22 §4
SD-044 | Solid | Sizing | Coated HX area, envelope-only basis | A_c |  | 10 | 13 | m² | superseded | T2 | Scales with the corrected duty | 22 §4
SD-045 | Solid | Sizing | Inventory multiplier, self-consistent duty | — |  | 3 | 5 | × | sizing-grade | T2 | Over the envelope-only row | 22 §4
SD-046 | Solid | Sizing | Inventory multiplier, F3 compounded | — |  | 1.25 | 1.5 | × | PENDING M2 | M2 | Applied on top of SD-045 | 22 §4
SD-047 | Solid | Hardware | DCHX volumetric duty | — | 90 |  |  | kW/m³ | reference |  | vs ~59 for packed granular beds; 3–5× heat-transfer rate | 22 §1
SD-048 | Solid | Synthesis | Al₂(SO₄)₃·18H₂O, bench batch | m | 166.6 |  |  | g | procurement-grade | T1 | MW 666.43; 0.50 mol Al → ~75 g MOF (validation 41.7 g / full 5.5 kg) | 21 §3
SD-049 | Solid | Synthesis | Fumaric acid, bench batch | m | 58 |  |  | g | procurement-grade | T1 | MW 116.07; 0.50 mol (validation 14.5 g / full 1.9 kg) | 21 §3
SD-050 | Solid | Synthesis | NaOH, bench batch | m | 40 |  |  | g | procurement-grade | T1 | MW 40.00; 1.00 mol → 1:1:2 mole check (validation 10 g / full 1.3 kg) | 21 §3
SD-051 | Solid | Synthesis | DI water, bench batch | V | 750 |  |  | mL | procurement-grade | T1 | ~190 mL for the validation batch | 21 §3
SD-052 | Solid | Synthesis | Precipitation temperature | T | 60 |  |  | °C | procurement-grade | T1 | Hold 30–60 min; wash 3–4× DI; dry ~100 °C | 21 §3
SD-053 | Solid | Synthesis | LAG liquid ratio | η |  | 0.1 | 1 | µL/mg | developmental | T1 | Route B; 1 Al : 1 fumarate, no base | 21 §4
SD-054 | Solid | Synthesis | LAG aging temperature | T_age |  | 110 | 120 | °C | developmental | T1 | The aging step does much of the crystal growth | 21 §4
SD-055 | Solid | Synthesis | Ball-to-powder ratio (mill path) | BPR |  | 10 | 30 | × | developmental | T1 | Mill path only; mill-zero is mortar-and-pestle | 21 §4
SD-056 | Solid | Synthesis | Full-charge synthesis scale | m | 2.5 |  |  | kg | indicative | T2 | Mill returns at scale-up — hand-grinding does not scale | 21 §3
SD-057 | Solid | Bench rig | Coupon loop flow | V̇ |  | 0.5 | 1.5 | L/min | procurement-grade | M3 | Hot-water-rated DC pump; all-Al + SS wetted path, distilled water | 22 §5
SD-058 | Solid | Bench rig | Hot reservoir range | T |  | 50 | 90 | °C | procurement-grade | M2 | Sous-vide circulator as the precision hot source | 22 §5
SD-059 | Solid | Bench rig | Cold reservoir range | T |  | 10 | 25 | °C | procurement-grade | M1 | Ambient / ice-bathed | 22 §5
SD-060 | Solid | Bench rig | Capacitive RH sensor validity ceiling | T | 60 |  |  | °C | procurement-grade |  | Spec'd 20–80% RH; drifts ~+3% RH in sustained saturation → use wet/dry bulb | 22 §7
SD-061 | Solid | Bench rig | Durability cycle count | N_cyc |  | 100 | 1000 | cycles | requirement | M4 | Capacity fade + coating mass loss/delamination | 22 §6
CO2-001 | Shared | Spec P17 | Cabin CO₂ limit, all modes | c_CO2 | 1000 |  |  | ppm | requirement | J | Safety-critical; includes sealed operation | 00 §5
CO2-002 | Shared | Spec P17 | Alarm + forced boost threshold | c_CO2 | 2000 |  |  | ppm | requirement |  | Per-room max sensing governs the interlock | 00 §5
CO2-003 | Shared | Ventilation | CO₂ generation, 4 occupants awake | V̇_CO2 | 0.072 |  |  | m³/h | reference |  | Crew total, not per person (0.047 asleep); ≈3.4 kg/day | 00 §5
CO2-004 | Shared | Ventilation | CO₂ mass generation, 4 occupants | ṁ_CO2 | 3.4 |  |  | kg/day | reference |  |  | 00 §5
CO2-005 | Shared | Ventilation | Fresh-air floor | V̇_f | 48 |  |  | m³/h | requirement |  | 12 m³/h·person; mechanical minimum stop on the damper | 00 §5
CO2-006 | Shared | Ventilation | Steady CO₂ at 48 m³/h (awake) | c_CO2 | 1920 |  |  | ppm | sizing-grade |  | ABOVE the <1,000 spec — closed by the layer stack, not by ventilation | 00 §5
CO2-007 | Shared | Ventilation | Steady CO₂ at 48 m³/h (asleep) | c_CO2 | 1400 |  |  | ppm | sizing-grade |  |  | 12 §1
CO2-008 | Shared | Ventilation | Steady CO₂ at 36 m³/h | c_CO2 | 2420 |  |  | ppm | sizing-grade |  | Dose–response ladder — why the interlock exists | 00 §5
CO2-009 | Shared | Ventilation | Steady CO₂ at 24 m³/h | c_CO2 | 3420 |  |  | ppm | sizing-grade |  |  | 00 §5
CO2-010 | Shared | Ventilation | Steady CO₂ at 12 m³/h | c_CO2 | 6420 |  |  | ppm | sizing-grade |  |  | 00 §5
CO2-011 | Shared | Ventilation | Sealed envelope (infiltration only) | c_CO2 | 7600 |  |  | ppm | sizing-grade |  |  | 00 §5
CO2-012 | Shared | Ventilation | Closed-room penalty over main space | Δc |  | 2000 | 2900 | ppm | sizing-grade |  | Drives displacement ducting + per-room NDIR sensing | 00 §5
CO2-013 | Shared | Ventilation | Marginal heat cost of fresh air (ε 0.8) | e | 0.06 |  |  | kWh/day per m³/h | sizing-grade | E | (1−ε)×10.4 g/kg — makes generous ventilation cheap (X7) | 00 §5
CO2-014 | Shared | Ventilation | Heat saved per 12 m³/h cut (bare fresh) | E | 3.8 |  |  | kWh/day | sizing-grade |  | The standing economic temptation the interlock forecloses | 00 §5
CO2-015 | Shared | CO₂ battery | Scrubbing duty at the ventilation floor | ṁ_CO2 | 1.6 |  |  | kg/day | PENDING J | J | Two-bed solid-amine TSA in the recirculation branch | 00 §5
CO2-016 | Shared | CO₂ battery | Bed mass, amine (each of two) | m_b | 3 |  |  | kg | PENDING J | J | ~90-min half-cycles | 00 §5
CO2-017 | Shared | CO₂ battery | Recirculation flow through the bed | V̇ | 91 |  |  | m³/h | PENDING J | J | At 50% single-pass capture; +50–150 Pa | 00 §5
CO2-018 | Shared | CO₂ battery | Amine regeneration temperature | T_reg |  | 85 | 95 | °C | PENDING J | J | Off the same heat bus; solar-window schedulable | 00 §5
CO2-019 | Shared | CO₂ battery | Specific regeneration energy | e |  | 1 | 1.3 | kWh/kg | PENDING J | J | Includes water co-adsorption + sensible | 12 §1
CO2-020 | Shared | CO₂ battery | Daily regeneration heat | E |  | 1.6 | 2.5 | kWh/day | PENDING J | J |  | 12 §1
CO2-021 | Shared | CO₂ battery | Overnight stored obligation | m | 0.3 |  |  | kg | sizing-grade | J | Loaded beds hold the night → regeneration is schedulable | 00 §5
CO2-022 | Shared | CO₂ battery | Optimal bed placement humidity | RH |  | 45 | 55 | % | procurement-grade | J | Post-dehumidification; near-optimal for amine chemistry | 00 §5
CO2-023 | Shared | CO₂ battery | Potash (K₂CO₃/carbon) bed mass | m_b |  | 4 | 5 | kg | PENDING J-K | J-K | At ~0.5–0.65 mmol/g working capacity | 00 §5
CO2-024 | Shared | CO₂ battery | Potash regeneration temperature | T_reg |  | 130 | 150 | °C | PENDING J-K | J-K | Requires a ≥~130 °C tap; equilibrium-dead below ~120 °C (X11) | 00 §5
CO2-025 | Shared | CO₂ battery | Potash working capacity | q |  | 0.5 | 0.65 | mmol/g | PENDING J-K | J-K | Alumina and MgO supports prohibited — double-salt deactivation | 00 §5
CO2-026 | Shared | Fallback | Oversized ERV + DCV flow | V̇_f |  | 120 | 190 | m³/h | sizing-grade | E | → 800–1,000 ppm, open conditions only, no sealed guarantee | 00 §5
CO2-027 | Shared | X9 galley | Burner CO₂ emission, 2 kW | V̇_CO2 | 0.26 |  |  | m³/h | reference |  | 3.6× the whole crew — the reason for no combustion in the envelope | 00 §5
CO2-028 | Shared | X9 galley | Burner combustion water | ṁ_w | 0.25 |  |  | kg/h | reference |  | Latent load added on top of the CO₂ | 00 §5
CO2-029 | Shared | X9 galley | Induction galley electrical | E_e | 2 |  |  | kWh/day | sizing-grade |  | Deletes both burner terms | 00 §5
CO2-030 | Shared | Rejected | Raw-water CO₂ absorption flow | V̇ | 6 |  |  | m³/h | rejected |  | Fully equilibrated, slow kinetics, re-humidifies the air | 12 §5
CO2-031 | Shared | Rejected | Membrane driving pressure | ΔP | 0.1 |  |  | kPa | rejected |  | Cabin-ppm partial pressure — no membrane process closes | 12 §5
CO2-032 | Shared | Rejected | Algae/plant light demand | P | 150 |  |  | kWh/day | rejected |  | For 3.4 kg/day | 12 §5
CO2-033 | Shared | Rejected | Soda lime / LiOH consumable rate | ṁ | 15 |  |  | kg/day | emergency only |  | Emergency consumable, never an architecture | 12 §5
CO2-034 | Shared | Rejected | Electrochemical capture (watch item) | e | 1 |  |  | kWh_e/kg | R&D watch |  | In principle; not procurable at scale | 12 §5
CO2-035 | Shared | Rejected | CALF-20 capacity at cabin ppm | q |  | 0.1 | 0.17 | mmol/g | rejected |  | Selectivity ceiling ~40–47% RH straddles the bed placement | 12 §5
CO2-036 | Shared | Rejected | SIFSIX-class capacity / water co-adsorption | q | 1.25 | 7.5 | 10 | mmol/g | rejected |  | ppm-capable at ~1.2–1.3, but 7.5–10 mmol/g water rides every swing | 12 §5
CO2-037 | Shared | Rejected | Mg-MOF-74 humid capacity retention | — | 16 |  |  | % | rejected |  | Water poisons and hydrolyzes the open metal sites | 12 §5
CO2-038 | Shared | Rejected | Moisture-swing AER displaced heat | E |  | 5 | 15 | kWh/day | rejected |  | vs 1.6–2.5 for TSA — an X8 rule-1 violation at DP-A | 12 §5
IN-002 | Platform | Heat cascade | Two-stage HDH humidifier grade | T |  | 75 | 85 | °C | sizing-grade |  | Below the potash rung, above the amine rung | 30 §2
IN-003 | Platform | Heat cascade | HDH gained output ratio | GOR |  | 2.2 | 2.8 | — | sizing-grade |  | Warm sink pinches the cold end to ~34 °C — lab GOR-4+ does not transfer | 30 §3
IN-004 | Platform | Heat cascade | HDH yield per unit heat | V̇ | 90 |  |  | L/day·kW | sizing-grade |  | Raw-water feed sites only; never pointed at cabin air | 30 §3
IN-005 | Platform | Heat cascade | HDH stranded humidity at pinch | ω | 35 |  |  | g/kg | sizing-grade |  | Desiccant polish stage recaptures +20–25% when heat is free | 30 §3
IN-006 | Platform | Heat cascade | Resistive-HDH energy penalty vs RO | — | 27 |  |  | × | reference |  | Clipped-solar dump load and last resort only | 30 §2
IN-007 | Platform | Heat cascade | Marine RO specific energy | e |  | 4 | 20 | Wh/L | reference |  | The honest benchmark for deliberately manufactured water | 20 §7
IN-008 | Platform | Sources | PVT thermal grade | T |  | 45 | 50 | °C | procurement-grade |  | Cannot reach HDH grade; F2-dead for direct solid-bed regen | 30 §2
IN-009 | Platform | Sources | PVT panel mass | m | 36 |  |  | kg | procurement-grade |  | Beyond two panels the marginal thermal output has no user | 30 §4
IN-010 | Platform | Sources | ETC collector band | T |  | 60 | 93 | °C | procurement-grade |  | The liquid track's full grade band (X2) — the solar comfort island | 30 §2
IN-011 | Platform | Water ladder | Solid-track condensate surplus | V̇ |  | 50 | 70 | L/day | sizing-grade | T2 | Independent of HDH hardware — a real redundancy path | 30 §5
IN-012 | Platform | Water ladder | Liquid-track still distillate | V̇ |  | 8 | 18 | L/day | sizing-grade | G | The solar-independent path; also the M-cycle feed | 30 §5
IN-013 | Platform | Comfort | Conductive cooling pad duty | Q |  | 70 | 90 | W | sizing-grade |  | Sleeping; skin 33–35 °C vs 29 °C sink through a Ti/CuNi plate HX | 30 §3
IN-014 | Platform | Raw water | Marine intake depth | d |  | 5 | 10 | m | procurement-grade |  | For stability and cleanliness, NOT temperature (mixed layer isothermal to 20–40 m) | 30 §3
IN-015 | Platform | Marine | Design heel / roll | θ |  | 15 | 20 | ° | requirement | I, H | Flooded-mode fallbacks, staged headers, anti-slosh rules | 00 §1
IN-016 | Platform | Marine | Passive fluid-path heel rating | θ | 30 |  |  | ° | requirement |  | Thermosyphons, wicked heat pipes, trapped siphons, check-valved backups | 30 §7
IN-017 | Platform | Interface | Cascade tap — liquid-track sealed still | T |  | 60 | 93 | °C | requirement | D | Interface requirement on any source; grade from LQ-067 / IN-010 (X2) | 30, function statement
IN-018 | Platform | Interface | Cascade tap — solid-track regeneration | T |  | 60 | 65 | °C | requirement | M2 | Interface requirement on any source; grade from SD-024 (F2) | 30, function statement
IN-019 | Platform | Interface | Cascade tap — potash CO₂ bed where primary | T | 130 |  |  | °C | requirement | J-K | Interface requirement, platform-conditional; grade from CO2-024 (X11). Stated as a floor (≥ ~130 °C) | 30, function statement
UP-001 | Upgrade | X12 AHT | Absorption heat transformer COP | COP |  | 0.45 | 0.48 | — | estimate-grade | L | Upgraded heat ÷ driving heat, before losses | 31 §2.4
UP-002 | Upgrade | X12 AHT | Evaporator temperature | T_ev |  | 60 | 65 | °C | estimate-grade | L | The waste tail itself, boiling distillate at ~20–25 kPa | 31 §2.2
UP-003 | Upgrade | X12 AHT | Absorber (delivered) temperature | T_abs |  | 85 | 90 | °C | estimate-grade | L | Amine-bed regen grade + hot-regen still grade | 31 §2.2
UP-004 | Upgrade | X12 AHT | Gross temperature lift | ΔT |  | 20 | 25 | K | estimate-grade | L |  | 31 §2.3
UP-005 | Upgrade | X12 AHT | Lift ceiling, 44 wt% @ T_ev 65 °C | T_abs | 91 |  |  | °C | estimate-grade | A, L | aw(x)·Psat(T_abs) < Psat(T_ev); 85–86 °C at T_ev 60 °C | 31 §2.3
UP-006 | Upgrade | X12 AHT | Lift ceiling, 42 wt% @ T_ev 65 °C | T_abs | 86.5 | 86 | 87 | °C | estimate-grade | A, L | 81 °C at T_ev 60 °C | 31 §2.3
UP-007 | Upgrade | X12 AHT | Tail heat per unit upgraded heat | — | 2.2 |  |  | kW/kW | estimate-grade | L | ~5 kWh/day tail delivers the CO₂ battery's 2–2.5 kWh/day at grade | 31 §2.4
UP-008 | Upgrade | X12 AHT | Distillate lift pump head | ΔP | 16 |  |  | kPa | estimate-grade |  | Watt-scale peristaltic — unlike LiBr machines' solution pump | 31 §2.2
UP-009 | Upgrade | X12 AHT | Absorption latent release | h | 2.6 |  |  | MJ/kg | reference |  | Released at the brine's temperature — the whole X12 finding | 31 §2.1
UP-010 | Upgrade | VC heat pump | Electrical draw | P_e |  | 350 | 500 | W | estimate-grade | I | 5× step over the 25–80 W baseline — boost mode only | 31 §3
UP-011 | Upgrade | VC heat pump | Evaporator duty | Q_ev |  | 0.8 | 1 | kW | estimate-grade | I | 0.66 kW absorption heat + parasitic ingress through the contactor | 31 §3
UP-012 | Upgrade | VC heat pump | Condenser output | Q_c |  | 1.1 | 1.5 | kW | estimate-grade |  | Covers the 0.92 kW regen peak with surplus into the buffer | 31 §3
UP-013 | Upgrade | VC heat pump | Real heating COP at ~55 K lift | COP_h |  | 2.5 | 3 | — | estimate-grade |  | Small hermetic, inverter-driven | 31 §3
UP-014 | Upgrade | VC heat pump | Net floor gain at 20 °C brine | Δω |  | 3.5 | 4.5 | g/kg | estimate-grade | A, I | Most of the LiCl/hot-regen benefit for ~400 W and no new chemistry | 31 §3
UP-015 | Upgrade | VC heat pump | Glycol-loop approach penalty | Δω |  | 1.5 | 2 | g/kg | estimate-grade |  | Cost of the 2–3 K two-worlds isolation approach | 31 §3
UP-016 | Upgrade | VC heat pump | R290 condensing pressure at 70 °C | P | 2.6 |  |  | MPa | reference |  | Procurement winner: 0.5–1 kW HPWH rotaries; T_crit 96.7 °C | 31 §3
UP-017 | Upgrade | VC heat pump | R600a condensing pressure at 70 °C | P | 1.05 |  |  | MPa | reference |  | Best thermodynamic fit; charge 150–300 g, A3 flammable | 31 §3
UP-018 | Upgrade | Rejected | Prime-mover heat pump electrical draw | P_e | 2 |  |  | kW | rejected |  | At ~35 K sink-to-regen lift, COP_h 3.5–4 — loses to a VC-AC outright | 31 §1
UP-019 | Upgrade | Still MVR | Electrical draw at 0.88 kg/h | P_e |  | 110 | 140 | W | estimate-grade |  | PV-scale: makes the moisture battery rechargeable through a heat outage | 31 §4
UP-020 | Upgrade | Still MVR | Specific compression work | w |  | 120 | 160 | Wh/kg | estimate-grade |  | vs ~1,800 Wh/kg thermal | 31 §4
UP-021 | Upgrade | Still MVR | Headspace pressure, 70 °C / 42 wt% | P | 12.5 |  |  | kPa | estimate-grade |  | aw ≈ 0.40 — nearly half the pressure ratio is the activity depression | 31 §4
UP-022 | Upgrade | Still MVR | In-pool condensing pressure | P | 40 |  |  | kPa | estimate-grade |  | Sat. 76–78 °C for a useful 6–8 K ΔT → pressure ratio ~3 | 31 §4
UP-023 | Upgrade | Still MVR | Vapour volumetric flow | V̇ |  | 11 | 13 | m³/h | estimate-grade |  | At 12.5 kPa; PR ~3 excludes regenerative blowers (PR ~1.2 ceiling) | 31 §4
UP-024 | Upgrade | Still MVR | Compression superheat | ΔT |  | 80 | 90 | K | estimate-grade |  | Condensate-spray desuperheater ahead of the pool coil | 31 §4
UP-025 | Upgrade | AlFu chiller | Chilled-water cooling duty | Q_c |  | 0.9 | 1 | kW | estimate-grade | M-series | Holding brine at ~20 °C | 31 §5
UP-026 | Upgrade | AlFu chiller | Thermal COP | COP_th |  | 0.4 | 0.5 | — | estimate-grade | M-series | → 2–2.5 kW of 60–90 °C heat; +2–3 m² collector if solar-fed | 31 §5
UP-027 | Upgrade | AlFu chiller | Evaporator absolute pressure | P |  | 1.7 | 2 | kPa | estimate-grade | M-series | Leak-tightness is the make-or-break property | 31 §5
UP-028 | Upgrade | Crystallizer | Dihydrate CaCl₂ content | w | 75.5 |  |  | wt% | reference | A3 | CaCl₂·2H₂O | 31 §6
UP-029 | Upgrade | Crystallizer | Water uptake per kg dihydrate | Δm |  | 1.1 | 1.2 | kg/kg | estimate-grade | A3 | vs 0.143 kg/kg for the 40→35 wt% liquid swing | 31 §6
UP-030 | Upgrade | Crystallizer | Reserve mass reduction | — |  | 3 | 5 | × | estimate-grade | A3 | Occupied-night charge 35–40 kg → 10–15 kg | 31 §6
UP-031 | Upgrade | Crystallizer | Supercooling without seeding | ΔT |  | 10 | 20 | K | reference | A3 | Crystals never travel — the pot is isolated by a valve pair | 31 §6
UP-032 | Upgrade | PCM | CaCl₂·6H₂O melting point | T_m |  | 29 | 30 | °C | reference |  | Sits essentially at the sink temperature at DP-A — logged, low priority | 31 §6.2

## Psychrometrics
Psychrometrics — Magnus formulation
The shared basis under every number in the repository. The saturation table below reproduces doc 00 §2; the converter is a working tool for new states.
FORMULATION
Saturation pressure | P_sat(T) = A·exp(B·T/(T+C)) kPa, with A 0.61094, B 17.625, C 243.04 (Alduchov–Eskridge)
Humidity ratio | ω = 0.622·P_v/(P_atm − P_v), kg/kg — reported here in g/kg dry air
Dew point | T_dp = C·ln(P_v/A)/(B − ln(P_v/A))
Moist-air enthalpy | h = 1.006·T + ω·(2501 + 1.86·T) kJ/kg dry air
Why it matters | At DP-A every ambient sink sits at or above the 28.1 °C dew point — a sink-cooled condenser harvests ≈0 water and evaporative cooling cannot pass the dew point. Only a desiccant breaks that floor (doc 00 §3)
SATURATION TABLE — validated against doc 00 §2
T (°C) | P_sat (kPa) | ω_sat calc (g/kg) | ω_sat doc 00 (g/kg) | Δ (%) | Check |  | Note
20
21
22
23
24
25
26 |  |  | 21.3
27 |  |  | 22.6
28 |  |  | 24.1 |  |  |  | ≈ the DP-A dew point — the floor every ambient sink sits above
29 |  |  | 25.6 |  |  |  | Saturated working-air exhaust state in the solid balance
30 |  |  | 27.1
31
32
33
34
35
36
37
38
39
40
STATE CONVERTER — enter any two of T / RH / ω
State | T (°C) | RH (—) | ω (g/kg) | P_v (kPa) | T_dp (°C) | h (kJ/kg) | Note
Ambient DP-A | 32 | 0.8 |  |  |  |  | Ambient — the governing point
Cabin, liquid target | 29 | 0.55 |  |  |  |  | ω 13.8 g/kg published
Cabin, solid steady state | 25 | 0.4 |  |  |  |  | ω ≈ 9.1 g/kg published
Absorber outlet, base brine | 30 | [5 empty] | Floor set by sump concentration, not per-pass approach
Absorber outlet, hot-regen brine | 30 | [5 empty] | 43–44 wt%, aw 0.34
ERV-dried fresh air | 31 | [5 empty] | Pre-dried from ambient at ε_lat
Solid supply air | 17.5 | [5 empty] | M-cycle product on dried air
Working exhaust (saturated) | 29 | 1 |  |  |  |  | Recycled in X8 mode, never vented
BRINE FLOOR MATRIX — ω_out = f(aw, brine T) [PENDING test A]
Brine T (°C) ↓ / aw → | 0.33 | 0.34 | 0.4 | 0.45 | 0.5 | Published anchor
27 | [5 empty] | 10.0 @ aw 0.45 · 7.5 @ aw 0.34
28
29
30 | [5 empty] | 11.9 @ aw 0.45 · 9.0 @ aw 0.34
31
32
33 | [5 empty] | 14.2 @ aw 0.45
Published floors are 'sizing-grade, PENDING test A'. Published data carries ±0.05 aw, which is ±1.5–3 g/kg on the floor — the largest single unknown in the liquid track (doc 12 §3). Cooling leverage 0.5–0.7 g/kg per K of brine cooling is the slope of each column.

## Model 00§4
The generalized airflow–moisture model (doc 00 §4)
The closed steady state that replaced the hand-chained state tables — the origin of finding F1 and the 9–11 kg/h solid-track duty. Solved live for three working-air topologies.
THE SIX EQUATIONS (doc 00 §4)
Equation 1 | ω_cab = ω_sup + latent_gains / S (cabin steady state)
Equation 2 | T_sup = T_in − ε_dp·(T_in − T_dp(ω_work)) (M-cycle on dried air)
Equation 3 | S = Q_sens / (c_p·(T_cab − T_sup)) (supply flow closes the sensible load)
Equation 4 | Q_wet = S·c_p·(T_in − T_sup) (heat dumped into the wet channel)
Equation 5 | M = Q_wet / Δh_work, Δh_work = h_sat(T_exh) − h(entry) (working-air flow)
Equation 6 | duty = (S − M)(ω_cab − ω_sup) + M(ω_amb − ω_sup) (sorbent duty)
Why it matters | Omitting the M-cycle working-air moisture term under-sizes the desiccant 3–5×. At DP-A the 29 °C sink cannot absorb heat from a 25 °C cabin, so ALL cabin sensible load leaves evaporatively — and that moisture must pass through the desiccant. This is finding F1.
INPUTS
Sensible load Q_sens |  | kW | Doc 20 §1, peak sun
Latent gains |  | kg/h | Occupants + envelope; doc 20 uses 2.0 kg/h total incl. envelope
Envelope + occupant latent (doc 20 basis) | 2 | kg/h | The value doc 20 §5 actually solves with
Supply humidity ratio ω_sup |  | g/kg | AlFu back-end — the model's only sorbent input
Intake temperature T_in | 31 | °C | Post-ERV fresh / mixed state entering the desiccant
Cabin temperature T_cab |  | °C | Solid-track target
M-cycle effectiveness ε_dp |  | —
Working exhaust temperature |  | °C | Saturated at the sink
Ambient ω |  | g/kg | DP-A
SOLUTION BY TOPOLOGY — the working air's entry state is the design choice
Quantity | Dry-draw (post-desiccant) | Cabin-draw (open cycle) | X8 closed loop (recycled exhaust) | Unit | Published (doc 20 §5) | Δ vs published | Check | Note
Working-air entry ω |  | 9.1 |  | g/kg |  |  |  | Dry-draw and X8 re-dry to ω_sup. Cabin-draw carries CABIN humidity, which the model also solves — so this cell is a seed; the residual row below reports convergence
Working-air entry T |  |  |  | °C |  |  |  | X8 re-dries AND intercools the recycled exhaust exactly like the process stream (doc 20 §2), so its entry state matches dry-draw; only the moisture it carries differs
Working-air dew point |  |  |  | °C |  |  |  | Equation 2's floor — the M-cycle cannot pass it
Supply temperature T_sup |  |  |  | °C | 17.45 |  |  | Published band 16.8–18.1 °C (midpoint quoted here)
Supply flow S |  |  |  | kg/s | 0.47 |  |  | Published band 0.43–0.51 kg/s (≈1,350–1,590 m³/h)
Supply flow, volumetric |  |  |  | m³/h | 1470
Cabin ω (equation 1) |  |  |  | g/kg | 9.1 |  |  | Doc 20 §5: ~9.1 g/kg ≈ 40% RH — drier than target, headroom exists
Cabin RH at that state |  |  |  | — |  |  |  | 9.1 g/kg at 25 °C is ~46% RH, not the ~40% quoted in doc 20 §5 — still inside the 40–55% comfort band, so no design consequence. See CHK-010
Wet-channel heat Q_wet |  |  |  | kW |  |  |  | Equation 4 — the heat that must leave evaporatively
Exhaust enthalpy (saturated) |  |  |  | kJ/kg |  |  |  | h_sat at the sink temperature
Working-air entry enthalpy |  |  |  | kJ/kg
Δh_work |  |  |  | kJ/kg |  |  |  | Equation 5's denominator
Working flow M |  |  |  | kg/s | 0.145 |  |  | Published band 0.13–0.16 kg/s (400–500 m³/h)
Working flow, volumetric |  |  |  | m³/h | 450
Sorbent duty (equation 6) |  |  |  | kg/h | 10 |  |  | Published 9–11 kg/h — finding F1
Regeneration heat |  |  |  | kW | 8.25 |  |  | Published 7.5–9 kW
Moisture desorbed per day |  |  |  | L/day |  |  |  | Doc 20 §5 publishes 150–220 L/day of RECOVERED condensate — lower than the desorbed total because part of the moisture leaves with the ventilation exhaust rather than reaching the condenser
X8 closure penalty (vs same-topology open) |  |  |  | × |  |  |  | Closure re-dries saturated exhaust (25.6 g/kg) instead of taking ambient makeup (24.2 g/kg), so the working term rises by that ratio alone. Doc 20 §8 quotes a +10–16% raw swing 'partly bought back by the colder dry-draw supply and the ERV'd ventilation term' — this sheet lands at about +7%
Convergence residual (seed − solved cabin ω) |  |  |  | g/kg |  |  |  | Cabin-draw only: how far the seeded working-air entry ω sits from the solved cabin state. Re-enter the solved value in the seed cell (or enable iterative calculation) until this reads ~0
READING THE RESULT
Both open topologies land inside the published 9–11 kg/h band, and the published supply-temperature band (16.8–18.1 °C) turns out to be exactly the span between them — dry-draw at the cold end, cabin-draw at the warm end. Cabin-draw is the doctrinal choice (finding X5: route makeup through the cabin before it becomes working air), and it also delivers the ~600 ppm CO₂ that doc 20 §2 describes as a structural by-product of open-cycle operation. The X8 column re-dries the saturated exhaust instead of taking ambient makeup, which costs about +7% on duty here — consistent with doc 20 §8's '+16% swing, partly bought back'. The reason closure is nearly free at DP-A is visible in two numbers: ambient sits at 24.2 g/kg and saturated exhaust at 25.6 g/kg. In any milder ambient that gap widens and closure is what makes the M-cycle water-neutral.
Circularity note: equations 1–6 are mutually dependent (S ← T_sup ← ω_work ← M ← Q_wet ← S). This sheet closes the loop by fixing each topology's working-air ENTRY state, which is the physical design choice, and solving in one pass. Enable iterative calculation in your spreadsheet application if you want to relax the cabin-draw entry humidity onto the solved cabin state rather than the published one. The full transient model (task T2) supersedes this steady state — it does not replace it.

## Liquid Sizing
Liquid track — mixed-mode sizing (docs 10–12)
The 0.88 kg/h peak, the regeneration budget, the reserve, and the rejection duty, re-derived live from DP-A. Blue cells are inputs.
AIR PATH — mixed mode (X6): CO₂-interlocked fresh minimum + recirculated bulk
Fresh air (CO₂ floor) |  | m³/h | Mechanical minimum stop — never a control setting
Fresh air, mass basis |  | kg/h | Doc 12 quotes ≈58 kg/h
Recirculated air | 75 | m³/h | Doc 10 §2; decouples removal from the ventilation ration
Recirculated air, mass basis |  | kg/h | Doc 12's build-up implies 90.6 kg/h
Total absorber flow |  | m³/h | Doc 12 quotes ~123 m³/h (≈147 kg/h) — see CHK-001
Total absorber flow, mass basis |  | kg/h
ABSORBER FLOOR — set by sump concentration, not per-pass approach
Brine water activity (aw) |  | — | PENDING test A — ±0.05 aw is ±1.5–3 g/kg of floor
Brine temperature |  | °C | Sink + approach; cooling is REQUIRED, not optional (erratum 2)
Absorber outlet floor ω |  | g/kg | Doc 12 publishes 11.9 g/kg at aw 0.45 / 30 °C
Published floor, base brine | 11.9 | g/kg | Doc 12 §1 — for comparison
Hot-regen floor ω (43–44 wt%) |  | g/kg | Doc 12 publishes 9.0 g/kg — the deep-dry lever without LiCl
REMOVAL DUTY — the 0.88 kg/h peak
Term | Calculated | Published | Δ | Check | Unit | Basis
Fresh-air term, bare intake |  | 0.713 |  |  | kg/h | 58 kg/h × (24.2 − 11.9) g/kg — the dominant term without an ERV
Recirculation term |  | 0.172 |  |  | kg/h | 90.6 kg/h × (13.8 − 11.9) g/kg — holds the cabin at target
PEAK REMOVAL, bare fresh |  | 0.88 |  |  | kg/h | Doc 12 §1 headline: 0.88 kg/h at DP-A, 4 adults, mixed mode
Fresh-air term, ERV'd at ε 0.8 |  | 0.232 |  |  | kg/h | ω_ERV 15.9 g/kg from doc 12 §1
PEAK REMOVAL, ERV'd at ε 0.8 |  | 0.49 |  |  | kg/h | Doc 12 publishes 0.49 kg/h — which reproduces at ε≈0.65 (ω 17.4), not ε 0.8. See CHK-002
Sanity: flow needed to hold 13.8 g/kg |  | 147 |  |  | kg/h | Gains 280 g/h ÷ (13.8 − 11.9) g/kg — reproduces the 147 kg/h figure
REGENERATION & HEAT REJECTION
Term | Calculated | Published | Δ | Check | Unit | Basis
Latent duty at peak removal |  | 0.6 |  |  | kW | removal × 2.44 MJ/kg
COP applied to the peak duty | 0.65 |  |  |  |  | Doc 12 §1 gives a COP build-up of ≈0.59 with no recovery HX and ~0.65 with one. The published 0.92 kW headline corresponds to 0.65, i.e. the recovery-HX case — see CHK-012
Regeneration heat, bare fresh |  | 0.92 |  |  | kW | latent ÷ COP; reproduces the published 0.92 kW at COP 0.65
Regeneration heat, ERV'd |  | 0.6 |  |  | kW | Does NOT reproduce: the published 0.6 kW needs both the ε 0.65 removal (CHK-002) and a COP near 0.55. The two ERV'd lines in doc 12 §1 are not on a single consistent basis
Absorption heat into the brine |  | 0.66 |  |  | kW | 0.88 kg/h × 2.7 MJ/kg — must be rejected or the contactor self-limits
Raw-water flow at 2 K rise |  | 300 |  |  | L/h | Doc 12: ~300 L/h base; 3–4 K rise halves the flow at ~1 g/kg of floor
Air-side heat removal, fresh stream only |  | 16 |  |  | W/K | Why an uncooled contactor warms 5–8 K and loses the floor — see CHK-004
Air-side heat removal, total flow |  | 35 |  |  | W/K | The ~35 W/K figure quoted in doc 10 §3 is on the mixed-mode flow
MOISTURE BATTERY & DAILY BUDGET
Water absorbed per kg concentrate |  | kg/kg | 0.40/0.35 − 1 = 0.143
Occupied-night duration | 12 | h | The reserve must bridge it with zero heat input
Duty-averaged fraction of peak | 0.55 | — | Night duty is below the DP-A peak (sleeping occupants)
Overnight concentrate draw |  | kg | Doc 10 §3 publishes ~35–40 kg; spec band 25–55 kg
Reserve tank spec, minimum | 25 | kg | Doc 10 §3
Reserve tank spec, maximum | 55 | kg
Duty-schedule factor over 24 h | 0.8 | — | Peak duty does not run all day; the published daily figures are duty-scheduled
Daily heat, bare fresh |  | kWh/day | Doc 12 publishes 17–20 kWh/day
ERV + DCV reduction factor | 0.54 | — | Ratio of the published ERV'd budget to the bare-fresh budget (10 ÷ 18.5 at midpoints)
Daily heat, ERV + DCV scheduled |  | kWh/day | Duty-scheduling and DCV take the bare-fresh budget down to the published 9–11 kWh/day; the ERV is ~9–10 kWh/day of that saving on its own (X7)
CONTACTOR SIZING
Cell rated capacity (mid-band) | 0.6 | kg/h | PENDING test I — published band 0.4–0.8 kg/h
Cells required at peak duty |  | cells | Doc 11: mixed-mode duty sits inside a 2-cell bank at mid-rating
Bank provision (+1 empty bay) |  | bays | One deliberately empty bay is design doctrine
Irrigation per cell | 9 | L/min | 150–240 L/min·m²; underwetting collapses K·a nonlinearly
Total irrigation demand |  | L/min | The binding constraint is wetting, not airflow
Face velocity | 0.8 | m/s | Band 0.6–1.0 m/s
Face area implied by total flow |  | m²

## Solid Sizing
Solid track — DCHX sizing (docs 20–22)
Duty → sorbent inventory → coated area → condensate balance, with the F3 effective-Δq penalty applied explicitly rather than buried.
DUTY (from the Model 00§4 sheet — cabin-draw solution)
Peak sorbent duty | 10 | kg/h | Published band 9–11 kg/h (F1); the model sheet re-derives it
Half-cycle time | 10 | min | Throughput is governed by cycle time and coated area, not mass
Water per half-cycle |  | kg
Modules alternating | 2 | — | One adsorbing while the other regenerates
SORBENT INVENTORY — the F3 penalty made explicit
Basis | Δq (g/g) | Inventory (kg) | Coated area (m²) | vs envelope-only | Grade | Note
Envelope-only (cautionary row) | 0.25 |  |  |  | superseded | The naive sizing error: ignores where the sensible heat goes
Self-consistent peak, dry-purge Δq | 0.25 |  |  |  | sizing-grade | Published 0.2–0.3 g/g — a DRY-PURGE full-swing figure (F3)
Self-consistent peak, effective Δq | 0.175 |  |  |  | PENDING M2 | 0.15–0.2 g/g after a 0.05–0.10 g/g residual at 60–65 °C — the real sizing number
Conservative (Δq floor) | 0.15 |  |  |  | PENDING M2 | The bottom of the F3 band
Doc 22 §4 states the self-consistent charge is 3–5× the envelope-only row (~3–4 kg / 10–13 m²), then +25–50% again once F3 compounds. The envelope-only inventory reproduces at 0.18 kg/m² planform (doc 22 §2), but the published 10–13 m² for that 3–4 kg implies ~0.3 kg/m² — the coated-area column therefore does not reconcile with the stated loading. See CHK-013.
ENERGY & WATER BALANCE
Term | Calculated | Published | Δ | Check | Unit | Basis
Latent floor of desorption |  | 6.7 |  |  | kW | 0.67 kWh/L — material-independent, 70–85% of the input
Regeneration heat, total |  | 8.25 |  |  | kW | 0.85 kWh/L × duty; published band 7.5–9 kW
Daily regeneration heat |  | 198 |  |  | kWh/day | Continuous duty at DP-A — why this track is waste-heat-coupled
Moisture desorbed per day |  |  |  |  | L/day | Doc 20 §5 publishes 150–220 L/day of RECOVERED condensate. The desorbed total is higher because part of the moisture leaves with the ventilation exhaust rather than reaching the condenser train
Condensate recovered (published basis) | 185 |  |  |  | L/day | Midpoint of the published 150–220 L/day
Potable-grade surplus | 60 |  |  |  | L/day | Published 50–70 L/day: the gains + ventilation terms
M-cycle wet-channel feed |  |  |  |  | L/day | What the condensate must cover for the loop to close
DHW heat recoverable | 2 |  |  |  | kWh/day | Demand-capped 1–3 kWh/day — first in the doc 00 §7 rule-4 recapture order
DHW recovery as a fraction of input |  |  |  |  | — | Doc 20 §3 quotes '~10–15% recoverable as useful energy' but the DHW cap it cites in the same sentence (1–3 kWh/day) is only ~1% of the daily regeneration input at this duty. The two statements are on different bases — see CHK-015
REGENERATION AGAINST HUMID PURGE — why 60–65 °C, not 50 °C (F2)
Bed temperature (°C) | P_sat at bed (kPa) | Purge P_v (kPa) | RH at bed face | Doc 20 §6 | vs AlFu step ~25–30% | Verdict
45 |  |  |  | 38%
50 |  |  |  | 29%
55
60 |  |  |  | 17%
65 |  |  |  | 13%
70
Purge humidity ω (condensing purge) | 25 | g/kg | The single input that decides the whole heat-source question. AlFu's often-quoted '~50 °C regeneration' is a DRY-purge figure and does not transfer. M2 is run against a logged ~24 g/kg purge, never dry lab air. Note: doc 20 §6's own RH column back-solves to ~23 g/kg rather than the ~25 g/kg its text states — at 23 g/kg the 50 °C row reads 29% and is 'on the step' rather than above it (CHK-012).
SYNTHESIS SCALING (doc 21 §3, aqueous route) — 1 Al : 1 fumarate : 2 NaOH
Reagent | MW (g/mol) | Validation ~19 g | Bench ~75 g | Scaled to charge | Unit | Note
Al₂(SO₄)₃·18H₂O | 666.43 | 41.7 | 166.6 |  | g | Verify hydrate assay per lot COA
Fumaric acid | 116.07 | 14.5 | 58 |  | g | FCC / E297 grade
NaOH | 40 | 10 | 40 |  | g | Add to water slowly — strongly exothermic
DI water |  | 190 | 750 |  | mL | mL, not g
Mole check (bench): 0.50 mol Al : 0.50 mol fumarate : 1.00 mol NaOH = 1 : 1 : 2
Target MOF mass | 2.5 | kg | Full charge is ~2.5 kg indicative; hand-grinding does not scale to it

## CO2 & Ventilation
CO₂ & ventilation — the four-layer stack (doc 00 §5, spec P17)
SAFETY-CRITICAL. <1,000 ppm at all times in every mode including sealed; alarm and forced boost at 2,000 ppm; per-room maximum sensing; mechanical minimum stop.
DOSE–RESPONSE LADDER — c = c_out + 10⁶·V̇_CO₂/V̇_fresh
Fresh air (m³/h) | Per person (m³/h) | CO₂ awake (ppm) | Doc 00 §5 | Δ | CO₂ asleep (ppm) | vs spec | Note
124 | [6 empty] | X8 mode: ventilation sized for the spec, +10–15% duty at solid-track scale
91
48 |  |  | 1920 |  |  |  | The ventilation floor — above spec on its own; the layer stack closes it
36 |  |  | 2420
24 |  |  | 3420
12 |  |  | 6420 |  |  |  | Per-person floor if the interlock were defeated
6 | [6 empty] | Illustrative only — below any legal minimum
Sealed envelope (infiltration only) reads ~7,600 ppm; a closed room runs +2,000–2,900 ppm over the main space, which is why sensing is per-room and the interlock keys to the MAXIMUM reading, not an average.
LAYER 1 — ERV ECONOMICS (X7)
ERV latent effectiveness ε |  | — | PENDING test E; purchasable with membrane area
Moisture gradient ambient − cabin |  | g/kg | Doc 00 quotes 10.4 g/kg
Unrecovered moisture per kg fresh |  | g/kg | The (1−ε)×10.4 term
Marginal heat, ERV'd |  | kWh/day per m³/h | Doc 00 quotes 0.06 — this sheet reproduces the order
Marginal heat, bare fresh |  | kWh/day per m³/h | Doc 00's '3.8 kWh/day per 12 m³/h' is this bare figure — see CHK-003
Heat saved per 12 m³/h, bare basis |  | kWh/day | Doc 00 quotes ~3.8 kWh/day
ERV saving at the 48 m³/h floor |  | kWh/day | Doc 11 §5 / X7 quotes ~9–10 kWh/day. This sheet lands higher because it runs the full peak-duty gradient for 24 h; the published figure is duty-scheduled, like the daily budgets on the Liquid Sizing sheet. Either way it is the single largest lever on the heat budget
CO₂ crossover (EATR) limit | 0.05 | — | Acceptance limit, test E — an ERV must not recycle CO₂
LAYER 2 — THE CO₂ BATTERY (X10 amine / X11 potash) — REQUIRED-PENDING tests J / J-K
Quantity | Amine (solar grade) | Potash (waste-heat) | Unit | Published | Check |  | Note
Regeneration temperature | 85–95 | 130–150 | °C |  |  |  | Potash is equilibrium-dead below ~120 °C; the ETC's 93 °C ceiling cannot regenerate it
Scrubbing duty at the floor |  |  | kg/day | 1.6 |  |  | Chemistry-agnostic: the duty is set by the crew and the ventilation rate
Bed mass, each of two |  |  | kg |  |  |  | Amine ~3 kg; potash 4–5 kg at 0.5–0.65 mmol/g working
Half-cycle |  |  | min | 90
Recirculation through the bed |  |  | m³/h | 91 |  |  | At 50% single-pass capture; +50–150 Pa
Specific regeneration energy |  |  | kWh/kg |  |  |  | Amine 1.0–1.3 incl. water co-adsorption + sensible
Daily regeneration heat |  |  | kWh/day | 2.05 |  |  | Published 1.6–2.5 kWh/day — schedulable into the solar window
Overnight stored obligation |  |  | kg | 0.3 |  |  | Loaded beds carry the night
Bed placement humidity | 45–55 | 45–55 | % RH |  |  |  | Post-dehumidification. Carbonation WANTS this band — water is a reagent
Breathing-air gate | amine/ammonia slip (J) | alkaline carryover (J-K) | — |  |  |  | Safety register item 4 — gates any connection to breathing air
Support prohibition | — | alumina, MgO | — |  |  |  | Irreversible double-salt deactivation
LAYER 0 — X9: WHY THERE IS NO GAS IN THE ENVELOPE
Crew CO₂, 4 occupants awake |  | m³/h | The whole design load
One 2 kW gas burner | 0.26 | m³/h | 3.6× the entire crew
Burner ratio to crew |  | × | Doc 00 §5 quotes 3.6×
Burner combustion water | 0.25 | kg/h | A latent load on top of the CO₂
Induction galley cost |  | kWh_e/day | Deletes both terms — safety register item 2
LAYER 3 — INTERLOCK: CO₂-governed fresh damper with a MECHANICAL minimum stop, so no controller fault or economy setting can close ventilation below the floor. Recirculation-only operation is prohibited while occupied. Scrubbing never substitutes for the ventilation floor. Each 12 m³/h of fresh air cut saves ~3.8 kWh/day of heat — a standing economic temptation that the mechanical stop, not software, forecloses.

## Heat & Water
Platform heat cascade & water ladder (doc 30)
Match each load to the grade of heat it needs; spend high grade only at the cascade bottom. Water comes from heat, air, or sky — not meaningfully from electricity.
HEAT-GRADE CASCADE
Rung | Grade (°C) | Load | Served by | Note
Source | high (continuous) | Electricity generation | High-grade process heat | Single point of failure for water AND power simultaneously
1 | 130–150 | K₂CO₃ CO₂-bed regeneration (X11) | Process tail | Only on platforms with a ≥~130 °C tap
2 | 75–85 | Two-stage HDH humidifier | Process tail | The water engine at saline-feed sites; never pointed at cabin air
3 | 85–95 | Amine CO₂ bed + hot-regen still | Process tail · ETC · X12 AHT | The grade an AHT can synthesise from a 60–65 °C tail
4 | 60–93 | Liquid-track regeneration | ETC solar 2.5–4.5 m² | The solar comfort island — X2 keeps driving force positive across the whole band
5 | 60–65 | Solid-bed regeneration | Waste-heat tail (primary) | F2: solar-direct is equilibrium-dead here against a condensing purge
6 | 45–50 | PVT thermal output | PVT ×2 | Cannot reach HDH grade; F2-dead for direct solid-bed regeneration
Sink | ~29 | Rejection | Raw water | Adsorption heat releases only a few K above the sink — reject it, don't chase it
LIQUID-TRACK DAILY HEAT BUDGET & SOURCE SIZING
Daily regeneration heat (ERV + DCV) | 10 | kWh/day | Published band 9–11 kWh/day
CO₂-battery regeneration | 2.05 | kWh/day | Published 1.6–2.5 kWh/day (test J)
Domestic hot water draw | 2 | kWh/day | Demand-capped 1–3 kWh/day — first in the recapture order
Total thermal demand |  | kWh/day
Solar yield per m² per day | 2.75 | kWh/m²·day | 2.5–3 kWh/m²·day basis
Collector area required |  | m² | Published 2.5–4.5 m² flat-plate class
Diesel heating value | 8.5 | kWh/L | 5 kW hydronic heater class
Diesel-only fuel burn |  | L/day | Published 1.1–1.4 L/day at full DP-A duty
Induction galley electrical | 2 | kWh_e/day | X9 — a battery/inverter sizing line on a solar-only island
System electrical, scaled | 65 | W | Published 50–80 W band including ERV and exhaust fans
Daily electrical, comfort system |  | kWh_e/day
WATER REDUNDANCY LADDER — independence is the property that matters
Path | Source class | Independent of HDH? | Rate | Unit | Role | Note
Process-heat HDH | raw water + free heat | — (is the HDH) | high | L/day | primary | GOR 2.2–2.8 at a 29 °C sink; ~90 L/day per kW of heat
Resistive-HDH | raw water + battery electricity | NO — common mode | high | L/day | heat-source backup only | Shares columns, raw-water loop, and air loop; ~27× RO's energy per litre
Solid-track condensate | humid air + low-grade heat | YES | 50–70 | L/day | comfort byproduct | X8 custody; water-neutral M-cycle in every ambient
Liquid-track distillate | humid air + solar-grade heat | YES | 8–18 | L/day | solar-independent path | Also the M-cycle feed — the loop closes
Rain catchment | sky | YES | generous, intermittent | — | passive | Over-invest here: it is the cheapest independent path
Emergency RO (pickled) | raw water + small power | YES | drinking + essentials | — | dormant | The only path robust OUTSIDE the humid tropics; few cycles → minimal fouling
Fresh-water tanks | — | YES | buffer | — | autonomy | Bridges any outage; the other cheap independent path
Common-mode warning: process-heat HDH and resistive-HDH share columns, the raw-water loop, and the air loop — resistive backs up heat-source loss only. Real security lives in the mechanically independent paths, and the cheapest of those (tankage and rain) is where to over-invest. Redundancy outranks efficiency in the field.

## Upgrade Paths
Upgrade paths — boost modes only (doc 31)
BINDING RULE: every path here is an addition, never core. No DP-A comfort, air-quality, or water claim may depend on any of them; the baseline must remain fully operable with every one removed. All figures estimate-grade — nothing here has been bench-tested.
X12 — CaCl₂ ABSORPTION HEAT TRANSFORMER · the lift-ceiling inequality, solved live
Governing inequality: aw(x) · P_sat(T_abs) < P_sat(T_evap) — absorption stays downhill only while the brine's depressed vapour pressure sits below the evaporator's.
Strong brine | aw | T_evap 60 °C → T_abs max | Doc 31 §2.3 | T_evap 65 °C → T_abs max | Doc 31 §2.3 | Check (65 °C) | Note
44 wt% | 0.34 |  | 85.5 |  | 91 |  | The deliverable: a ~20–25 K gross lift into the 85–90 °C band
43 wt% | 0.37 |  | 83 |  | 88.5
42 wt% | 0.4 |  | 81 |  | 86.5 |  | Below hot-regen still grade — concentration is the lever
40 wt% | 0.45 |  | 77 |  | 83 |  | Base brine cannot reach amine-bed grade
The ceiling is real and single-stage: the X11 potash rung (130–150 °C) is beyond reach. Test A's measured aw table feeds this inequality directly — the ±0.05 aw uncertainty on the brine side propagates straight into the lift ceiling.
X12 — ENERGY BALANCE
AHT thermal COP | 0.465 | — | 0.45–0.48 before losses: upgraded heat ÷ driving heat
Upgraded heat required (amine bed) | 2.25 | kWh/day | The CO₂ battery's 1.6–2.5 kWh/day at 85–95 °C
Driving tail heat drawn |  | kWh/day | Doc 31 quotes ~5 kWh/day
Heat rejected via the still condenser |  | kWh/day | Through hardware already running
Continuous form |  | kW tail per kW upgraded | Doc 31 quotes ~2.2
Distillate lift pump head | 16 | kPa | Watt-scale peristaltic — unlike LiBr's solution pump
Absorption latent release | 2.6 | MJ/kg | Released AT the brine's temperature — the X12 finding
STILL MVR — the pressure ratio decomposition (doc 31 §4)
Pool temperature | 70 | °C
Brine concentration | 42 | wt% | aw ≈ 0.40 at this concentration
Water activity at that concentration | 0.4 | — | PENDING test A
Pure-water saturation at pool T |  | kPa | What the headspace would be over pure water
Actual headspace pressure |  | kPa | Doc 31 quotes ~12.5 kPa
Required in-pool condensing pressure | 40 | kPa | Sat. 76–78 °C for a useful 6–8 K ΔT
Pressure ratio |  | — | Doc 31 quotes ~3
Ratio attributable to activity depression |  | — | The machine pays for the desiccant's aw as pressure ratio — the compression-side mirror of X12
Specific compression work | 140 | Wh/kg | vs ~1,800 Wh/kg thermal
Electrical at 0.88 kg/h peak duty |  | W | Doc 31 quotes 110–140 W — PV-scale
THE FAMILY AT A GLANCE — and the recorded rejection
Path | Character | Converts | Into | Cost | First gate | Platform trigger | Note
X12 AHT (§2) | heat-only, no new chemistry | 60–65 °C waste tail | 85–90 °C process heat | COP 0.45–0.48 | test L | waste-heat tail ≤65 °C | PRIMARY upgrade — the still is half the machine
Coupled VC heat pump (§3) | electron-rich boost | ~350–500 W electric | brine floor depth + regen heat | +3.5–4.5 g/kg | procurement + test I | electron-rich, heat-poor | Most of the LiCl benefit for ~400 W and no new chemistry
Still MVR (§4) | heat-outage regenerator | ~110–140 W electric | full still duty, no heat source | 120–160 Wh/kg | compressor mist pre-gate | electron-rich | Makes the moisture battery rechargeable on electricity alone
Closed AlFu chiller (§5) | heat-rich boost | 2–2.5 kW solar/waste heat | heat-driven brine chilling | COP_th 0.4–0.5 | solid M-series + leak-down | heat-rich, electricity-poor | Closed cycle → no purge → X2-clean: the solid chemistry finally works on solar heat
Static crystallizer (§6) | mass-limited platforms | reserve tank mass | 3–5× denser moisture battery | 35–40 → 10–15 kg | test A3 (~$10) | marine mass-limited | Crystals never travel — the pot is valve-isolated
REJECTED: heat pump as prime mover | — | ~2 kW electric | regeneration-grade heat | COP_h 3.5–4 | — | none | Loses outright to a 1–3 kW VC-AC and abandons the heat-flexibility proposition

## Test Program
Test program — cheapest decisive experiment first
Every PENDING grade in the register points at a row here. The budget sums live: change the in-baseline flag and the total follows.
Baseline gating budget |  |  |  |  | USD |  | Live sum of the tests flagged in-baseline above. The former '~$485–755' aggregate headline was retired in doc 12 v1.4 — it did not decompose from the table and a currency-and-date-specific total dates badly in a prior-art record. Read every cost here as 2026 order-of-magnitude, one currency, one region.
All listed tests |  |  |  |  | USD |  | Including the platform-conditional entries (A2, A3, C, J-K, L) that join the set only when their trigger exists. Solid-track T/M entries carry no cost line in the documents — they are effort, plus outsourced PXRD/DVS fees.
ID | Track | Title | Cost lo | Cost hi | Duration | In baseline | What it measures | What it decides
A | Liquid | Jar equilibrium — real aw table | 30 | 30 | days | yes | Sealed jars + RH probe over CaCl₂ 35/38/40/42/44 wt% (+LiCl arm) at ~27 and ~33 °C | Go/no-go: 40 wt% @ 33 °C ≤ 55% ERH. Feeds every floor number and the X12 lift inequality
A2 | Liquid | Aerated hot coupon (formate variant) | 20 | 20 | weeks | no | Whether potassium-formate brine survives aerated 80 °C service | Materials relaxation for that variant only
A3 | Upgrade | Crystallizer jar extension | 10 | 10 | days | no | Seeded vs unseeded 44 wt% parked at ~25 °C: supercooling, phase, caking over 50–100 cycles | Gates the static crystallizer pot (doc 31 §6); mass-limited platforms only
B | Liquid | Aerosol drift — steel coupon | 5 | 5 | 1 week | yes | Bare mild-steel coupon downstream of eliminator + demister, max face velocity, trickle and flooded | Any rust = redesign before any cabin connection. Also arbitrates X3 (safety register item 3)
C | Liquid | Bubble column / sparger shootout | 150 | 150 | weeks | no | Sparger dynamic wet pressure comparison | Only if the column annex is ordered
D | Liquid | Regeneration COP | 50 | 50 | days | yes | Still tray + air-swept at 60/70/85 °C incl. the PVC-tray 60 °C point and condenser approach | Confirms the 0.55–0.75 COP band and the degraded ladder
E | Liquid | ERV core | 80 | 150 | weeks | yes | Real ε_lat; salt-aerosol fouling trend (U-tube ΔP); condensation at DP-A inlet; CO₂ crossover | Gates the 9–11 kWh/day heat budget (X7); EATR <5%
F | Liquid | Endurance (passive) | 0 | 0 | months | yes | Locker/closet-dryer duty: salt creep, fouling, crystallization events, ΔP trend | Runs behind everything else at zero cost
G | Liquid | Sealed-still rate | 40 | 40 | days | yes | kg/h·m² vs pool temperature; condensate TDS (entrainment ≈ 0); TDS on the air-swept condenser stream | Gates distillate quality claims and the X8 degraded-mode condensate
H | Both | M-cycle wetting / heel | 60 | 60 | days | yes | Supply temp vs feed humidity; 5/10/15° tilt; closed-loop feed point (X8 recycled dried exhaust) | Shared verbatim with the solid track — one experiment serves both
I | Liquid | Film cell prototype — THE GATE | 150 | 250 | weeks | yes | Outlet RH vs irrigation rate FIRST; 1/2/3-stage NTU/m; face velocity incl. the ~123 m³/h point; rocking rig 5–20°; flooded run | The liquid gate: if the capacity model holds, the bank build proceeds
J | Shared | CO₂ sorbent (amine) | 150 | 300 | weeks | yes | Capacity at 1,000–1,500 ppm / 45–55% RH; desorption completeness 85–95 °C; water co-adsorption; amine/ammonia slip; fade over 10²–10³ cycles | Required-PENDING: gates X10 entirely and the breathing-air connection. Fallback = oversized ERV + DCV
J-K | Shared | CO₂ sorbent (potash variant) | 40 | 80 | weeks | no | K₂CO₃-on-apolar-carbon: capacity, regeneration at 120/135/150 °C with logged purge, alumina-deactivation control, caking, alkaline carryover, 10² cycles | Waste-heat platforms with a ≥~130 °C tap only (X11)
L | Upgrade | Hot-film absorption (AHT) | 60 | 120 | weeks | no | Absorption rate and approach of a 43–44 wt% film at 85/88/90 °C against ~20–25 kPa steam; drain-back-on-stop and a deliberate cool-in-place fault | Gates X12. Go/no-go: measurable absorption at 88–90 °C with test A's aw table confirming the margin
T1 | Solid | Mill-zero synthesis batch |  |  | days | yes | Mortar-and-pestle ~25 g LAG batch with the F4 feedstock branch pre-loaded | Stage 0 of the staged pipeline
T2 | Solid | Full airflow–moisture transient model |  |  | weeks | yes | Supersedes the doc 00 §4 steady state; sets charge, coated area, condenser duty, fan power | Gates every downstream solid size — the first modelling task before hardware
T3 | Solid | RH / DAQ channel budget |  |  | days | yes | Wet/dry-bulb + K-type channel plan before M2 (second logger or unified ESP32 node) | On the critical path for M2
T4 | Solid | Outsourced PXRD + DVS |  |  | weeks | yes | Phase match to A520 and the Type V step at 25–30% RH | The real pass/fail gate on synthesis (QC gates 3 and 5)
T5 | Solid | Coating SOP |  |  | weeks | yes | PVA grade locked, anneal mandatory, adhesion and capacity retention | Runs on the commercial A520 lot so coating never blocks on synthesis
T6 | Solid | Bench M1–M4 |  |  | weeks | yes | M2 against a representative ~24 g/kg purge → effective Δq | Gates the heat-source decision and the inventory
T8 | Solid | Silica-wheel benchmark quote |  |  | days | yes | Commercial wheel sized to the T2 duty | The fallback at any gate — and the honest benchmark
T9 | Solid | Commercial Basolite A520 lot |  |  | days | yes | 25–100 g buy-to-validate lot | Parallel path: coating work proceeds independently of synthesis
M1 | Solid | Adsorption working capacity + coated-face ΔP |  |  | days | yes | Weigh activated-dry coupon → saturate isothermally → reweigh; U-tube manometer at design face velocity | ΔP gates the 0.6–1.0 kW fan-power line
M2 | Solid | Regeneration vs representative humid purge |  |  | weeks | yes | One 45–50 °C confirmation, then completeness and kinetics at 60/65/70 °C against a logged ~24 g/kg purge | THE most economically consequential measurement: confirms F2, extracts the F3 effective Δq
M3 | Solid | Specific regeneration energy |  |  | weeks | yes | Fluid-side balance Q = ∫ṁ·c_p·ΔT dt, dry blank first, then wet; condensate cross-check | vs the 0.67 kWh/L latent floor and 0.8–1.0 kWh/L total
M4 | Solid | Cycling durability + salt-air edge behaviour |  |  | months | yes | 10²–10³ swings, periodic M1 + dry-mass weigh, coating edge/defect inspection under salt aerosol | Capacity fade and coating mass loss — the failure mode that matters (F5)

## Findings
Findings register (doc 40)
Stable IDs — never renumbered. Any change to a sizing figure or architecture decision must be reflected here with its ID.
ID | Track | Finding | Consequence | Status | Lives in
F1 | Solid | M-cycle working-air moisture is the dominant latent term | Peak duty ~9–11 kg/h (not ~2); regen ~7.5–9 kW; condenser and fan duty scale with it. Closure: condensate covers M-cycle feed with ~50–70 L/day surplus | PENDING T2 (full transient sets the final charge) | 00 §4; 20 §5
F2 | Solid | Solar-direct regeneration is equilibrium-dead at the peak point | Against a condensing purge (~25 g/kg) a 45–50 °C bed faces 29–38% RH at its face — at/above AlFu's step. Waste heat primary; the liquid track is the solar comfort island | PENDING M2 (confirms; real deliverable is 60–65 °C completeness + effective Δq) | 20 §6
F3 | Solid | The sizing Δq is optimistic | 0.2–0.3 g/g is a dry-purge full-swing figure; a 0.05–0.10 g/g residual cuts effective Δq to 0.15–0.2 (+25–50% inventory), compounding F1 | PENDING M2 | 21 §6; 22 §4
F4 | Solid | Mill-zero needs a feedstock-reactivity branch | The literature mortar-and-pestle result used freshly precipitated amorphous Al(OH)₃; crystalline gibbsite is sluggish. A PXRD fail may be feedstock, not milling energy | PENDING T1/T4 | 21 §4
F5 | Solid | Aluminium DCHX in chloride service | Sealed/filtered intake, no dissimilar-metal fittings, coating as barrier layer, materials law imported; X8 closure is the primary mitigation | Corrosion rate PENDING M4 | 22 §3
F6 | Solid | The DCHX sensible-cycling bucket is unverified | Swung heat capacity per unit water swung is unspecified; if the allowance is optimistic, specific energy and continuous regeneration both move upward and bed-to-bed recovery becomes a hard requirement | PENDING M3 (M1 gates the coated-area denominator) | doc 40 F6; doc 20 §3–4; doc 22 §1
X1 | Shared | Once-through ventilation and whole-cabin M-cycle never compose | 5.5–11 kg/h absorber duty at DP-A; in recirc topology whole-cabin liquid AC converges to solid-track duty (~10.6 kg/h, ~11 kW) — deferred | settled | 00 §4/§6; 10 §2
X2 | Shared | Regeneration asymmetry is a theorem | The sealed still (no purge) keeps positive driving force at any pool >~40 °C; the solid bed hits F2's wall below ~50 °C → liquid = solar layer, solid = waste-heat layer | settled | 00 §3; 30 §2
X3 | Shared | Liquid desiccant for cabin air is re-scoped, not rejected | 'Rejected absent demonstrated aerosol control' — test B is the arbiter | PENDING B | 21 §2; 11 §3
X4 | Shared | Materials doctrine flows both ways | Nylon ban, brazed-plate prohibition, drip discipline and the sourcing heuristic imported to the solid track | settled | 22 §3
X5 | Shared | The airflow cascade | Route makeup through the cabin before it becomes working air. Berth scale: full 48 m³/h kept (1,920 vs 2,670 ppm), more cooling (102 vs 86 W), 1.6 °C supply cost | PENDING H | 10 §2; 20 §2
X6 | Liquid | Mixed-mode recirculation is the occupied baseline | Once-through fails 4-adult comfort at DP-A (59–66% RH); mixed-mode restores 55% at 0.88 kg/h. Recirc-only prohibited while occupied | PENDING I | 10 §2; 00 §5
X7 | Shared | ERV latent recovery on the fresh stream | (1−ε)×10.4 g/kg per kg; ε ≥0.8 saves ~9–10 kWh/day and makes generous ventilation cheap. Needs one ducted exhaust path; crossover <5% | PENDING E | 11 §5; 20 §2
X8 | Shared | Exhaust-vapour recovery doctrine | Saturated process exhausts end in distillation recovery; no stream is both rejection sink and recovery source; closed working loop = water-neutral M-cycle | design intent; PENDING H/G | 00 §7; 20 §8; 11 §4
X9 | Shared | All-electric galley — no combustion in the envelope | One 2 kW burner = 3.6× the crew's CO₂ + ~0.25 kg/h latent; induction costs ~2 kWh_e/day | settled (safety register 2) | 00 §5; 30 §4
X10 | Shared | The CO₂ battery | Two-bed solid-amine TSA, 85–95 °C regen, ~1.6 kg/day for ~1.6–2.5 kWh/day — the only path holding <1,000 ppm sealed | REQUIRED-PENDING J | 00 §5; 11 §5; 12 §4
X11 | Shared | Sealed-mode CO₂-bed chemistry is heat-grade-dependent | K₂CO₃/apolar-carbon TSA (130–150 °C) is the waste-heat-platform primary; the amine resin (85–95 °C) is the solar-grade bed; alumina/MgO supports prohibited | REQUIRED-PENDING J-K | 00 §5; 12 §4–6; 30 §2/§6
X12 | Upgrade | The brine's activity depression is a temperature lift | A single-stage CaCl₂ absorption heat transformer — sealed still unchanged as generator + condenser — upgrades a 60–65 °C tail to 85–90 °C at COP 0.45–0.48. Ceiling ≲91 °C single-stage | PENDING L — upgrade path only, never load-bearing | 31 §2; 40 §2
X14 | Shared | Thermal-swing sensible penalty is set by the inert-mass ratio, not by cycle time | Half-cycle duration cancels; the design levers are inert-mass-to-sorbent ratio and bed-to-bed recovery effectiveness, never cycle speed | settled | doc 40 X14; doc 20 §3–4; doc 22 §1
P17 | Shared | CO₂ specification (safety-critical) | <1,000 ppm at all times in all modes; alarm + forced boost at 2,000 ppm; per-room maximum sensing; mechanical minimum stop on the fresh damper | binding requirement | 00 §5/§8
CORRECTION-TRAIL PRINCIPLE (doc 40 §5)
Every erratum stays visible. Never cite a margin as a computed value; re-run every comfort claim when the design point moves; solve steady states simultaneously, never as hand chains. The correction trail is part of the design's credibility — and, for a defensive publication, part of the evidentiary record.
THE LIQUID-TRACK ERRATA TRAIL (doc 12 §2)
Erratum 1 | Regeneration heat overstated 2× in first-pass tables |  |  | Never cite a margin as a computed value
Erratum 2 | Absorber outlet is a band, not a point; cooling reclassified optional → REQUIRED
Erratum 3 | Diffuser dynamic wet pressure was missing from the column blower budget |  |  | Drilled rings win
Erratum 4 | Nylon removed from approved materials |  |  | CaCl₂ stress-cracks loaded polyamides
Erratum 5 | Crystallization threshold corrected: 40 wt% liquidus ~12–13 °C, not ~5 |  |  | Interlock restated at 42/43 wt%
Erratum 6 | Regen exhaust condensate: 53 °C dew point rains salty condensate |  |  | Sloped drip-leg routing mandatory
Erratum 7 | Sparger head constant 1.35–1.4 kPa per 10 cm at SG 1.4
Erratum 8 | Once-through could not deliver 4-adult comfort at DP-A (59–66% RH) |  |  | Re-run every comfort claim when the design point moves
Erratum 9 | The self-consistent steady state, not the hand chain, sizes the system |  |  | Hand chains drifted 15–30% on duty

## Safety & Materials
Safety register & materials law
BINDING. Any build omitting these departs from this design (doc 00 §8, doc 11 §1).
# | Requirement | Specification | Source
1 | CO₂ interlock | <1,000 ppm target · 2,000 ppm alarm/boost · per-room maximum sensing · mechanical minimum stop on the fresh damper | 00 §5; P17
2 | No combustion in the envelope | No gas or combustion appliances in the conditioned envelope (X9) | 00 §5; 30 §4
3 | Aerosol control before cabin connection | Drift eliminator + demister chain and a clean steel-coupon acceptance (test B) before any liquid contactor touches breathing air | 11 §3
4 | CO₂-sorbent breathing-air assay | Amine/ammonia slip (test J) for amine beds; alkaline particulate/mist carryover (test J-K) for carbonate beds | 00 §5; 12 §4
5 | Distillate potability | Independent water-quality test before regular consumption; air-swept-condenser water never enters potable or M-cycle service before a TDS assay clears it | 11 §4; 12 §4
6 | Crystallization interlock | 42 wt% high-SG cutoff unless brine ≥22 °C guaranteed; 43 wt% storage cap; drain-back-to-still on stop where an AHT absorber is fitted | 11 §4; 31 §2.6
7 | Two-worlds materials rule | Applied to every brine- or raw-water-wetted component; never relaxed for land installs — the desiccant itself is the chloride source | 11 §1; 00 §1
THE TWO-WORLDS MATERIALS LAW — everything brine- or raw-water-wetted is metal-free
Status | Materials | Rationale
Use freely | PVC (≤60 °C), CPVC (≤93 °C), PP, HDPE/PE/PE-RT, PEX, PVDF, titanium, EPDM, FKM, silicone, ceramic/alumina, glass, acetal (POM) | Brine and raw-water side is metal-free by rule
Never | Copper, brass, bronze; aluminium (incl. anodized); zinc/galvanized; mild steel; 304 SS; nylon/polyamide | CaCl₂ is a documented stress-cracking agent for loaded PA parts (erratum 4)
Marginal — do not design in | 316/316L | Brief splash only; never warm immersion or crevice geometry (threads, brazed channels, gasket lands)
Wetted fasteners | PP / PVC / PVDF only | Parts sold for pools/aquaculture/chemical dosing are probably right; plumbing parts hide brass
Prohibited assembly | Any brazed-plate exchanger (304 + copper braze) on brine or raw water | Glycol↔buffer isolation duty only
Membrane between worlds | Titanium heat exchangers only | Never let the two fluids mix
AHT absorber (85–90 °C brine) | PVDF or PP-with-margin; titanium extraction coil | Past comfortable CPVC territory (93 °C with no margin)
Solid-track loop | All-aluminium + stainless wetted path, distilled water, silicone tubing on the hot loop | Avoid brass — galvanic couple with the anodic Al plate
Rule of thumb: parts sold for pools, aquaculture, or chemical dosing are probably right; parts sold for plumbing hide brass. Titanium heat exchangers are the ONLY membrane between the two worlds — never let the fluids mix. These rules are never relaxed for land installs, because the desiccant itself is the chloride source.

## Checks
Consistency observations
Raised while compiling this register by re-deriving each published figure. These are observations for the authors, not errata — no document has been changed.
ID | Type | Where | Observation | What the arithmetic shows | Impact | Disposition
CHK-001 | Unit label | 12 §1 | Mixed-mode total absorber flow is given as '~123–147 m³/h' | 123 m³/h and 147 kg/h are the same quantity at ρ ≈ 1.2 kg/m³ (147/1.2 = 122.5); the removal build-up 58 kg/h fresh + 90.6 kg/h recirc = 148.6 kg/h confirms it | Low — presentational | RESOLVED v1.3 — doc 12 §1 restated as one quantity in two units
CHK-002 | Internal consistency | 10 §3 vs 12 §1 | ERV pre-dried fresh air is 17.4 g/kg in doc 10 §3 and 15.9 g/kg in doc 12 §1 | 15.9 = 24.2 − 0.8(24.2−13.8) at the specified ε 0.8; 17.4 corresponds to ε ≈ 0.65. The quoted ERV'd removal 0.49 kg/h reproduces only from 17.4 (ε 0.65); ε 0.8 gives 0.40 kg/h | Medium — affects the ERV'd duty line | OPEN — recorded as doc 12 §2 erratum 10 and in doc 40's make-or-break list; gated on test E
CHK-003 | Basis label | 00 §5 | '0.06 kWh/day per m³/h' (ε 0.8) and 'each 12 m³/h saves ~3.8 kWh/day' sit in the same paragraph | Both are correct but on different bases: 3.8/12 = 0.317 kWh/day·m³/h is the BARE-fresh figure; 0.06 is the ERV'd one. Ratio 5.3 ≈ 1/(1−ε) | Low — presentational | RESOLVED v1.2 — doc 00 §5 now labels both bases
CHK-004 | Basis label | 10 §3 vs 12 §1 | Air-side heat removal quoted as ~35 W/K (doc 10) and ~16 W/K (doc 12) | 16.2 W/K is 48 m³/h of fresh air; ~41 W/K would be the 123 m³/h mixed-mode flow. Both are ṁ·c_p at their own flow — not contradictory, but the flow basis is unstated in doc 10 | Low — presentational | RESOLVED v1.1 — doc 10 §3 now names the flow
CHK-005 | Budget arithmetic | README; 12 §4 | The '~$485–755 gates everything' headline does not decompose from the doc 12 §4 cost column | The plausible baseline set {A,B,D,E,F,G,H,I,J} sums to $565–885; dropping J gives $415–585. No subset reproduces 485–755 exactly (the range span, 270, matches no combination of the listed spans) | Medium — traceability | RESOLVED v1.4 — the aggregate headline is retired; per-test estimates retained and scoped as 2026 order-of-magnitude figures (doc 12 §4)
CHK-006 | Model reproduction | 00 §4; 20 §5 | Independent re-solve of the doc 00 §4 steady state | Reproduces the published band on both topologies (see the Model 00§4 sheet): cabin-draw gives T_sup 18.2 °C, S 0.508 kg/s, ω_cab 9.09 g/kg, M 0.142 kg/s, duty 9.8 kg/h; dry-draw gives T_sup 16.8 °C, S 0.425 kg/s, duty 9.6 kg/h. Both sit inside the published 9–11 kg/h, and regeneration heat lands at 8.2 / 8.3 kW against the published 7.5–9 kW | Informational — model confirmed | The published supply-temperature band 16.8–18.1 °C is exactly the span between the two topologies, which is worth stating explicitly in doc 20 §5
CHK-007 | Model reproduction | 12 §1 | Independent re-derivation of the 0.88 kg/h mixed-mode peak | 58 kg/h × (24.2−11.9) + 90.6 kg/h × (13.8−11.9) = 0.713 + 0.172 = 0.885 kg/h — exact | Informational — confirmed
CHK-008 | Model reproduction | 00 §5 | Independent re-derivation of the CO₂ dose–response ladder | c = 400 + 10⁶·V̇_CO2/V̇_fresh with V̇_CO2 = 0.072 m³/h reproduces 1,920 / 2,420 / 3,420 / 6,420 ppm and 1,400 ppm asleep exactly — confirming 0.072 m³/h is the four-occupant total, not per person | Informational — confirmed | RESOLVED v1.2 — doc 00 §5 labels the rate 'crew total', foreclosing a 4× misreading
CHK-009 | Basis constant | 12 §1 | Air mass flows imply a density of ~1.208 kg/m³ | 48 m³/h → 58 kg/h and 75 → 90.6 kg/h both back-solve to ρ = 1.208 kg/m³ (standard ~1.2 air, roughly 20 °C). Moist air at DP-A is ~1.145 kg/m³, so the published mass flows — and every duty derived from them — run ~5% high | Low — conservative direction | RESOLVED v1.2 — doc 00 §2 states the ρ 1.2 basis
CHK-010 | Stated value | 20 §5 | Cabin steady state given as '~9.1 g/kg / ~40% RH' | 9.1 g/kg at the 25 °C cabin target is ~46% RH (Pv 1.461 kPa against Psat 3.169 kPa). ~40% RH at 25 °C would be ω ≈ 7.9 g/kg | Low — no design consequence | RESOLVED v1.1 — doc 20 restated at ~46% RH throughout
CHK-011 | Model reproduction | 20 §8 | X8 closure penalty at DP-A | Re-drying saturated exhaust (25.6 g/kg) instead of ambient makeup (24.2 g/kg) raises the working term by ~8% and total duty by ~7% against the same-topology open cycle — consistent with doc 20 §8's '+16% swing, partly bought back' | Informational — confirmed | Confirms the doctrine's core claim: at DP-A ambient is nearly as wet as saturated exhaust, so closing the loop is nearly free
CHK-012 | Basis label | 12 §1; 20 §6 | Two figures quote a basis their arithmetic does not use | (a) The 0.92 kW peak regeneration heat needs COP 0.65 — the WITH-recovery-HX value — not the 0.59 build-up printed beside it (0.599/0.65 = 0.921). (b) Doc 20 §6's purge-RH column back-solves to ~23 g/kg, while the text beside it says '~25 g/kg' and M2 is specified at ~24 g/kg | Low — presentational | RESOLVED v1.3/v1.1 — doc 12 §1 names COP 0.65; doc 20 §6 records the table's purge basis
CHK-013 | Internal consistency | 22 §2 vs 22 §4 | Coating loading and the sizing table's coated area do not reconcile | Doc 22 §2 specifies ~0.18 kg sorbent/m² planform. The §4 envelope-only row pairs 3–4 kg with 10–13 m², which implies ~0.3 kg/m². At the stated 0.18 kg/m² the same inventory needs ~19 m² | Medium — sizing consequence | OPEN — doc 22 §4 open item and doc 40's make-or-break list; gated on M1, size from 0.18 kg/m² meanwhile
CHK-014 | Rounding | 20 §5 | Condensate quoted as 150–220 L/day against a 9–11 kg/h duty | Duty × 24 h gives 216–264 L/day desorbed, so the published condensate range implies that part of the moisture leaves with the ventilation exhaust rather than reaching the condenser — which is physically right but never stated | Low — presentational | RESOLVED v1.1 — doc 20 §5 separates the three
CHK-015 | Basis mismatch | 20 §3 | Heat-recovery fraction quoted two ways in one sentence | 'Only ~10–15% is recoverable as useful energy' sits beside 'capped by DHW demand (~1–3 kWh/day against 35+ kWh/day liberated)'. The DHW cap is ~3–8% of 35 kWh/day, and only ~1% of the ~200 kWh/day of regeneration input the corrected F1 duty actually implies. The 35 kWh/day figure also predates the F1 correction | Low — no design consequence | RESOLVED v1.1 — doc 20 §3 restated against the corrected F1 duty
CHK-016 | Sizing basis | 00 §5 | CO₂-battery duty of ~1.6 kg/day is a daily average, not the peak | Steady-state balance at the 48 m³/h floor: crew 3.42 kg/day all-awake, ventilation removes 1.37 kg/day at 1,000 ppm, so the bed must take 2.05 kg/day — 28% above the published 1.6. The 1.6 figure reproduces only on a 16 h awake / 8 h asleep average. The doc's own 91 m³/h at 50% single-pass capture independently implies 2.16 kg/day, agreeing with the peak rather than with 1.6 | HIGH — safety-critical spec | OPEN — P17 requires <1,000 ppm AT ALL TIMES, so bed mass and regeneration heat should be sized on the all-awake peak: restate as ~2.05 kg/day peak (1.6 average), scale the bed ~28%, and have test J measure working capacity at the peak rate
CHK-017 | Stated threshold | 00 §3 | X2's '~40 °C' still-crossover is the dilute-end figure only | aw·Psat(T_pool) > Psat(29 °C) gives a crossover of 39.8 °C at aw 0.55 (35 wt%, where regeneration starts), 43.6 °C at aw 0.45 (40 wt%), and 49.1 °C at aw 0.34 (43–44 wt% hot-regen). The single '~40 °C' figure holds only at the start of the concentration swing | Low — no design consequence | OPEN — the design pool is 60–93 °C, far above all three, so X2's conclusion is untouched. State the crossover as a function of target concentration, since it sets the minimum useful pool temperature in degraded mode
CHK-018 | Cross-track basis | 12 §1 vs 20 §1 | The two tracks assume latent gains differing ~7× for the same platform | Liquid uses 280 g/h (4 × 70 g/h occupants only); solid uses 1.8–2.8 kg/h 'envelope + occupant'. The 1.72 kg/h non-occupant remainder implies ~0.95 ACH on the solid cabin (~1.37 ACH on the liquid one), against the 0.05–0.15 ACH doc 12 §3 uses for the unattended liquid case and the 0.48 ACH mechanical ventilation floor. Neither track states an ACH | Medium — traceability | OPEN — bounded, not architecture-breaking: re-solving doc 00 §4 across gains of 0.64–2.8 kg/h moves duty only 8.8→10.3 kg/h, so F1 and the 9–11 kg/h band both survive. State one envelope-leakage assumption in doc 00 and let both tracks inherit it
CHK-019 | Internal consistency | 11 §2 | Cell rating, face-velocity band and NTU approach share no operating point | A 600×300×150 mm cell has a ~0.09 m² face. At the DP-A baseline (123 m³/h over a 2-cell bank) face velocity is ~0.19 m/s — well under the stated 0.6–1.0 m/s — while the 0.4–0.8 kg/h rating reproduces exactly at that baseline. At 0.6 m/s the same cell passes ~194 m³/h and, at the NTU-1.9 / 85% approach used to size contactor depth, would remove ~2.9 kg/h, far above its own rating | Medium — gated by test I | OPEN — reconcilable only at an approach efficiency that falls with face velocity, which is never stated. Test I already measures exactly this (outlet RH vs irrigation and face velocity, staged NTU/m). Publish the rating with its approach and flow, not as a bare kg/h
Method: each headline figure was re-derived independently from the stated basis using the Magnus formulation and the doc 00 §4 model, then compared with the published value. CHK-006 through CHK-008 record figures that reproduced exactly and are logged as confirmations, not defects. Per the repository's own doctrine (doc 50 §8), nothing here should be silently corrected — supersede with a version bump and leave the trail visible.

## Sources
Source document set
The lineage this register was compiled from.
Document | Version | Contents
00_platform_basis.md | v1.5 | Scope, DP-A, shared physics, airflow–moisture model, CO₂ stack, X8 doctrine, safety register
10_liquid_concept_physics.md | v1.1 | Brine principle, mixed-mode baseline, moisture battery, berth cascade, performance envelope
11_liquid_architecture_materials.md | v1.2 | Two-worlds law, film-cell bank, aerosol control, sealed still, ERV/CO₂ hardware, thermal bus
12_liquid_numbers_test_plan.md | v1.4 | Validated quantities at DP-A, errata trail, sensitivities, tests A–L, rejected CO₂ alternatives
20_solid_concept_system.md | v1.2 | Architecture, corrected F1 balance, regeneration-vs-purge physics, X8 closed loop, energy verdicts
21_solid_sorbent_synthesis.md | v1.0 | Isotherm-step selection, candidates, aqueous + LAG routes, F4 branch, QC gates
22_solid_module_validation.md | v1.2 | DCHX design, coating rules, F5 mitigations, bench rig, M1–M4, staged pipeline
30_integration_energy_water.md | v1.3 | Heat cascade, HDH, source roles, all-electric galley, water ladder, degraded operation
31_upgrade_paths_sorption_cycles.md | v1.0 | X12 AHT, coupled VC heat pump, still MVR, closed AlFu chiller, static crystallizer
40_findings_register.md | v1.8 | F1–F6, X1–X12, X14, spec P17, tasks, make-or-break bench list
41_bench_bill_of_materials.md | v1.0 | Bench procurement list: class-and-spec, cheapest-decisive-first; no system BOM (F6/F3 open)
50_defensive_disclosure_plan.md | v1.7 | Venue stack, repo formation, Zenodo procedure, metadata, version discipline
executive_summary.md | v1.4 | Standalone abstract for examiner-channel deposit; carries the concept DOI and repo URL
SCOPE & PROVENANCE
Reading order | 00 (shared basis) → 10–12 (liquid) → 20–22 (solid) → 30–31 (integration, upgrades) → 40 (findings) → 50 (disclosure)
Single source rule | Doc 00 is the single source for scope, design point, shared psychrometrics, the airflow–moisture model, the CO₂ stack, the X8 doctrine, and the safety register. Track docs reference it, never restate it
What this workbook is | A derived working artifact. The documents remain authoritative; where this workbook and a document disagree, the document wins and the Checks sheet records the discrepancy
What this workbook is not | Not a measurement record. No figure here is measured data unless its grade says so — and none currently does
Regeneration | python3 scripts/build_parameter_workbook.py [output.xlsx] — regenerate rather than hand-edit, so the register stays traceable to the documents
Licensing | Workbook content CC-BY-4.0 with the documentation; generator script MIT with scripts/
Disclosure | Open defensive publication · concept DOI 10.5281/zenodo.21544099 · version DOI 10.5281/zenodo.21544100 · no patents sought or held